## Work Plan BOGT Power
BOGT POWER AVAILABILITY IMPROVEMENT
|  |  |  | 2017 | [15 empty] | 2018
| ACTIVITY DESCRIPTION | Cost (F$) ('000) | SUPPORT TEAMS REQUIRED | SEPTEMBER |  |  | OCTOBER |  |  |  | NOVEMBER |  |  |  | DECEMBER |  |  |  | JANUARY |  |  |  | FEBUARY |  |  |  | MARCH |  |  |  | APRIL |  |  |  | MAY |  |  |  | JUNE
|  |  |  | WK 2 | WK 3 | WK 4 | WK 1 | WK 2 | WK 3 | WK 4 | WK 1 | WK 2 | WK 3 | WK 4 | WK 1 | WK 2 | WK 3 | WK 4 | WK 1 | WK 2 | WK 3 | WK 4 | WK 1 | WK 2 | WK 3 | WK 4 | WK 1 | WK 2 | WK 3 | WK 4 | WK 1 | WK 2 | WK 3 | WK 4 | WK 1 | WK 2 | WK 3 | WK 4 | WK 1 | WK 2 | WK 3 | WK 4
1 | Repair and commission 2MVA Black Start generator GD-110 at PSS-2 | 35
| Procure required spares |  | MTCE EXECUTION COMM. TEAM./C & P | [39 empty] | Awaiting spares delivery; Spares @ F$35k – PO 4510383995 EDD 19.11.2017, service @ F$0 to SEH | bar: SEPTEMBER WK 2 to NOVEMBER WK 3
| Repair and commision unit | [41 empty] | Support required from Danie and team | bar: NOVEMBER WK 4 to DECEMBER WK 1
2 | Replacement of GD-210 Control panel display screen | 8.33
| Replace screen with old unit of GD110 as temporary measure |  | C&P | [39 empty] | Done | bar: NOVEMBER WK 2
| Procure new HMI for GD210 | [41 empty] | Spares @ F$8.33k PO 4510386084 | bar: SEPTEMBER WK 2 to NOVEMBER WK 4
| Install and commision new HMI | [41 empty] | DIY | bar: DECEMBER WK 1
3 | Restoration/upgrade of OGGS fuel gas Superheater control panels | 44.8
| Troubleshooting and OEM correspondence |  | OEM/C&P | bar: OCTOBER WK 1 to OCTOBER WK 4
| Procurement of required spares for repair/upgrade | [41 empty] | Spares F$27.8k PO 4510390845, service estimate F$17k – OEM quote | bar: NOVEMBER WK 1 to JANUARY WK 4
| Raise contract for OEM field engineer mobilisation | [41 empty] | Specialist contract required. Follow up contract manager approval | bar: OCTOBER WK 2 to JANUARY WK 4
Repair and commision units | bar: FEBUARY WK 1 to FEBUARY WK 4
6 | Resolve clink synchronisation error/Upgrade SS300 Clink system | 300
| Resolve clink synchronisation and switchgear faults |  | MTCE EXECUTION COMM. TEAM. | [39 empty] | Support from Danie and team | bar: APRIL WK 4
| Procure PLCs and other required spares | [41 empty] | Awaiting CAPEX notional budget (Quote is F$300k | bar: NOVEMBER WK 4 to MARCH WK 4
| Mobilise OEM rep and perform upgrade | [41 empty] | Specialist contract required. Follow up contract manager approval | bar: MARCH WK 4 to APRIL WK 2
7 | Resolve Terminal UPS faults - PSS1 rectifier BC-00F07 and PSS2 UPS V02 | 8
| Resolve PSS-1 UPS Rectifier BC-00F07 Common and Current alarm fault |  | MTCE EXECUTION COMM. TEAM./C&P | [39 empty] | Support from Danie and team for PSS1 BC | bar: APRIL WK 4
Troubleshoot faults on V02 | bar: OCTOBER WK 1 to NOVEMBER WK 1
| Procure required spares for PSS2 UPS V-02 | [41 empty] | Awaiting PO creation | bar: NOVEMBER WK 2 to FEBUARY WK 4
Repair and commision unit | bar: MARCH WK 1
8 | Power Generation Critical spares | 150
| Develop and optimise critical spares listing - spare protection relays, motor control centers (MCC), HV/LV circuit breakers and spares for diesel generator Enercon control panels |  | C&P | bar: NOVEMBER WK 2 to NOVEMBER WK 4
Request quotes and carry out SAP coding | bar: NOVEMBER WK 3 to DECEMBER WK 1
Create PR/POs | bar: DECEMBER WK 2
Take deliveries | bar: MARCH WK 1 to MAY WK 4
| Total | 546.13
CLOSED
ONGOING
NOT STARTED