## Slide 1: Resolve High Pressure on CST – Export Pumps Discharge Header
Aja-Onu Uchenna
Production Unit Manager, Gbaran and Kolo Creek Operations

## Slide 2: Resolve High Pressure on CST – Export Pumps Discharge Header
From Export Pumps Train 1
From Export Pumps Train 2
10”
10”
Condensate Storage Tank
To TNP Liquid Export
12”
6”
6”
12”
55XZV310
55CHV-150
55CHV-151
BLV785
BLV784
55XZV110
55XZV210
BLV3001
BLV3000
BLV787
6”
55PV001
Expected: The Differential Pressure between Pressure upstream (P1) and downstream (P2) 55XZV310 and 55CHV-150&151 should be minimal when Train 1 Discharge Header is lined up to Common Discharge Header
Actual: Restricted flow across 55XZV310 and 55CHV-150&151 with high Differential Pressure of Circa 23 Bar between Pressure upstream (P1 @ 42 Bar) and downstream (P2 @ 19 Bar) 55XZV310 and 55CHV-150&151
Impact:
Unavailability of Train 1 to flow to TNP
Operational challenges
No significant deferment
P1
P2
Fig 1: Current Operating Condition at Site

## Slide 3: Resolve High Pressure on CST – Export Pumps Discharge Header
 | Description | Scenario | Implementation Priority/Rank | Criteria
Option 1a/b | Close 55XZV310 and resolve issue during September 2021 S/D Open 55XZV310 and flow Train 1 Production to both TNP and Train 2 Surge Vessel via CST | Continue Production | 1 | Negligible Deferment, Train 1 Available for Production and Easy to Plan/Execute
Option 2 | Replace identified Defective Valves with Spool Piece and resolve issue during September 2021 S/D | Unscheduled Shutdown due to Impaired Functionality | 2 | Deferment of circa 20,000 bbls of Oil and Condensate, Deferment of 50 MMScF of Gas, Trains 1 & 2 unavailable for 5 hours and Detailed Planning required and Complex to Execution
Option 3 | Line up existing Train 1 to Common Discharge Header, continue injecting to TNP and immediate inspection/repair of Valves |  | 3 | Deferment of circa 40,000 bbls of Oil and Condensate, Deferment of 100 MMScF of Gas, Trains 1 & 2 unavailable for 10 hours, Detailed Planning required and Complex to Execute

## Slide 4: Resolve High Pressure on CST – Export Pumps Discharge Header: Option 1a/b
From Export Pumps Train 1
From Export Pumps Train 2
10”
10”
Condensate Storage Tank
To TNP Liquid Export
12”
6”
6”
12”
55XZV310
55CHV-150
55CHV-151
BLV785
BLV784
55XZV110
55XZV210
BLV3001
BLV3000
BLV787
6”
55PV001
Option 1a: Close 55XZV310 and resolve issue during September 2021 S/D. Line Up existing Train 1 to CST and produce to TNP via Surge Vessel Train 2
Option 1b: Open 55XZV310 and flow Train 1 Production to both TNP and Train 2 Surge Vessel via CST. However, only circa 5,000bbl/d is produced to TNP.
Impact
Negligible impact on Production
Limited information available on Valves internal condition to aid Shutdown Planning and Execution
Option 1a
Oil and Condensate Production via Train 2 at a Gross Rate of circa 70,000 bbls/day.
Reduced production to Train 1 at circa 5,000 bbls/day to ensure immediate availability of Train 1. All inventory to Train 2 will be diverted to CST via Train 1 in the event of TNP Outage.
Option 1a/b has occurred before at the location
Option 1b
Consequence of further differential pressure increase across the CST – Export Pump Discharge Header resulting to complete restriction along the line.
Train 2 SV

## Slide 5: Resolve High Pressure on CST – Export Pumps Discharge Header: Option 2
From Export Pumps Train 1
From Export Pumps Train 2
10”
10”
Condensate Storage Tank
To TNP Liquid Export
12”
6”
6”
12”
55XZV310
BLV785
BLV784
55XZV110
55XZV210
BLV3001
BLV3000
BLV787
6”
55PV001
Option 2: Replace identified Defective Valves with Spool Piece and continue production to Common Export Header via Spool Piece until Shutdown. Install Repaired/Replacement Valves during Gbaran 2021 Shutdown
Shutdown Train 1 and Train 2 to enable Isolation
Remove 55XZV310 and 55CHV-150&151 for Repairs/Replacement
Install 6” Spool Piece
Start Up Train 1 and Train 2 to commence export to TNP via Common Export Header
Impact
Deferment of Circa 20,000bbls due to Train 1 and Train 2 oil and condensate Shutdown for 5 hours to enable isolation, removal of Valves and installation of Spool Piece.
Deferment of Gas for 5 hours – Circa 300 MMScF to enable Isolation, removal of valves and installation of Spool Piece.
Availability of information on Valves internal condition to aid Shutdown Planning and Execution
MoC required
Potential to breach SPDC JV Gas Supply to NLNG Agreement due to Gas Quality contaminated by Oil in the event of Spiking as a result of failure and removal of 55CHV-150&151

## Slide 6: Resolve High Pressure on CST – Export Pumps Discharge Header: Option 3
From Export Pumps Train 1
From Export Pumps Train 2
10”
10”
Condensate Storage Tank
To TNP Liquid Export
12”
6”
6”
12”
55XZV310
55CHV-150
55CHV-151
BLV785
BLV784
55XZV110
55XZV210
BLV3001
BLV3000
BLV787
6”
55PV001
Option 3: Line up existing Train 1 to Common Discharge Header, continue injecting to TNP and immediate inspection/repair of Valves
Shutdown Train 1 and Train 2 to enable Isolation
Reverse Spectacle Blind downstream BLV785 to Open
Close all Manual Valves from Train 1 Export Pumps to CST; BLV3000, BLV3001 etc to prevent back flow of Oil from Train 2 to CST via Common Header.
Remove 55XZV310 and 55CHV-150&151 for Inspection/Repairs
Blind Flange upstream 55XZV310 and downstream 55CHV-151
Start Up Train 1 and Train 2 to commence export to TNP via Common Export Header
Shutdown Train 1 and Train 2 post Inspection/Repair to reinstall 55XZV310 and 55CHV-150&151
Impact
Deferment of circa 20,000bbls due to Train 1 and Train 2 oil and condensate Shutdown for 5 hours to enable isolation and removal of Valves. Also for reinstallation.
Deferment of Gas for 5 hours, circa 300 MMScF to enable Isolation and removal of valves. Also for reinstallation.

## Slide 7: Resolve High Pressure on CST – Export Pumps Discharge Header
S/N | Scenario | Execution Readiness | Remarks
1 | Faulty Check Valves 55CHV-150 (Butterfly Valve) 55CHV-151 (Flapper Valve) | Check Valves unavailable at Site for Replacement Personnel available at Site for Repairs | 2 Nos required for Isolation To be sourced via Maintenance Execution Team [ONGOING]
2 | Faulty 55XZV310 Shutdown Valve | SDV unavailable at Site for Replacement Personnel available at Site for Repairs | To be sourced via Maintenance Execution Team
3 | 6” CL600 Blind Flanges required for Isolation | Blind Flanges unavailable at Site for Replacement | Available at IA Warehouse
4 | Spool Piece required for Replacement | Spool Piece unavailable at Site for Replacement Personnel available at Site for Construction | Scoping of required Spool Piece lengths completed at Site Spool Piece to be constructed at Site Piping available at Site Flanges to be sourced via Maintenance Execution Team [ONGOING]