## Slide 1: Tunu NODE DIY ACTIVITIES FOR Q1 2024 (cost avoidance)

## Slide 2: DIY in troubleshooting and restoration of Tunu Nodes Compressors by in-house resources as vendor specialist call out was initially planned and these issues had previously required vendor specialist call out to resolve them
PROBLEM STATEMENT :
Between last week of December 2023, OPUKUSHI Associated gas booster compressor (AGBC3) start-up sequence failure and flash gas compressor (FGC) software error preventing the units from starting resulted to an unscheduled deferment due to creaming and closed-in of wells for flare management. Ogbotobo Flash gas compressor error on Safety PLC Logix551S preventing the unit start up sequence from progressing. The in-house Tunu node resources mobilized, troubleshot and resolved the issues . Vendor call out was also initially planned to mobilize to site for intervention as these issues had previously required vendor specialist call out to resolve them., The node gained enormous savings by deploying in-house resources to resolve the issues
Activities carried out include:
OPUKUSHI:
Resolved the issue on the FGC safety partner controller. The firmware of the newly installed Allen Bradley Safety Partner 1756-L7SP was upgraded to be able to work with the Safety PLC Logix5571S
Resolved the UCP SIS communication failure to communicate with the Process PLC.
Loaded the logic to the Safety PLC Logix551S and commissioned it.
Installed back repaired Operation Workstation OWS CPU and restored the unit back to the Delta V DCS network.
Also troubleshot resolved and started up activities on AGBC 3
Ogbotobo;
Resolved error on Safety PLC Logix551S for Flash gas compressor.
Troubleshoot Safety PLC with Programing software error and clear all the errors, Safety PLC ready for start-up.
COST SAVINGS: (cost avoidance) impact from last week of December, 2023 to Q1 of 2024
Cost saving on Vendor (FSR) to site to resolve the above issues @ $70,000