## Slide 1
Fire & Gas System Cost Optimization
The EA Field Integrated Control and Safety System (ICSS) provides the full functionality for the control, monitoring and safe shutdown of Sea Eagle FPSO in the event of an emergency. The ICSS consists of the following sub-systems; Distributed Control System(DCS), Instrumented Protective System(IPS) and Fire& Gas System(FGS).
The FGS protection system comprises of the Topside Fire & Gas Hull Fire & Gas detection systems. The Topside Fire & Gas system uses the Infrared Line of Sight(LOS), Infrared Fixed Gas Detectors, Linear Heat Detection(Firewire) and Ultra -Violet(UV) Flame Detection System for fire and gas monitoring.
Below are high level details of Gas detectors failure rate on Sea Eagle;
There are 250 Searchpoint Optima Plus “Infrared Fixed Point Gas Detectors” with an Annual Failure Rate of about 8.8% = 22 Faulty Detectors/Year.
100 Searchline Excel “Line of Sight Gas Detectors” with an Annual Failure Rate of about 25% = 25 Faulty Detectors/Year.
The failure rates are largely age-related with an average of 85pcs of gas detectors being consumed /procured annually at a total cost of circa US$631,940.
There exists a significant cost saving opportunity through repair of the faulty detectors, instead of purchasing news ones. This repair will be carried out by the OEM, with a 12months repair warranty. The breakdown is contained in attached spreadsheet
Faulty Gas detector are being disposed off.
Failure rate is increasing due to ageing.
Average of 85pcs of gas detectors are procured annually at circa $631,940.00
Background / Business Case
Current Condition
Potential Benefits
Estimated cost savings up to circa US$448,640.00.
Certified Honeywell (OEM) Repairs.
12 Months repair warranty from date of repair.
Provision of calibration.
Honeywell Repair/diagnostic Report.
Use of Genuine Honeywell Components
Sign Off
Project Sponsor: Christopher Ugochukwu
Project Coordinator Boma Brown
Implementation Lead: Eyitayo Balogun
Project Team: Jude Igbinawan
    Alaba Ogundile
    Wilson Oborokumo
Milestone Deliverables
Key milestones: Date
Define Work Scope Q1 2021
Select Execution strategy Q1 2021
Secure budget Q1 2021
Finalise OEM/Vendor engagement Q1 2021
Create PO Q2 2021
Carry out pilot repair & return Q2 2021
Review outcome of pilot and deploy fully Q3 2021