## Slide 1: Gbaran ESD Investigation
SPDC

## Slide 2
What Happened?(Incident description)
Why it Happened (Causal Theory)
Validation of Causal Theory
Recommendations
Content

## Slide 3: Problem Statement
Expected: Gbaran CPF to continue uninterrupted production of 1BScF/d of gas and 35kbopd of liquid.
Actual: Gbaran CPF tripped on ESD 2.5.1B from metering house fire and gas alarm on 1st September 2020 at 848am.
Impact: Deferred volume of 347.06MMScF gas and 6,896.09bbl liquid.

## Slide 4: What Happened?
Date | Time | Description/Activity
1st September 2020 | 8:48:26am | Low Level Gas Confirmed Alarm Acknowledged from 1 of 4 OPGDs (74QS575)
 | 8:48:28am | Low Gas Trip Acknowledged from 1 of 4 OPGDs (74QS576)
 | 8:48:30am | High Gas Trip Acknowledged from 1 of 4 OPGDs (74QS576)
 | 8:48:32am | ESD 2.5.2 was initiated (Blowdown of Metering Train 1, Train 2 Lines, Shutdown of AGCs)
 | 8:48:32am | Trip signal sent to the 3 GTGs but GTGs remained running
 | 10:29:00am | Plant Restarted after ESD 2.5.2 trip

## Slide 5: Why it happened
GAS DETECTION
There was fugitive emissions from surrounding pipe-work
High earthing resistance (11.83ohms) led to build up of electrostatic charges in signal cable
The electrostatic buildup amplified the signal level on 74 QZA- 576 to within the trip limit
This led to a high level gas trip signal sent to the SIS inter-trip logic (74XZ913)
GTG FAILURE TO TRIP
ESD 2.5 sent trip signal to GTG as per cause and effect as-built design.
The ESD 2.5 trip signal failed to activate a trip of the GTG.
The trip signal loop between the HIMA SIS and GTG was discovered disconnected.

## Slide 6: Validation of Key Cause of Failure.
  GAS DETECTION
  There was an actual gas concentration of 0.697 LEL
  The Trip limit for a high gas trip is between 1 and 3 LEL
The earth resistance of 74-QZA-576 was 11.83ohms (Shell Benchmark < 4 Ω)
GTG FAILURE TO TRIP
  Inter-trip signal from HIMA SIS to GTG confirmed from alarm catalogue post activation of ESD 2.5 shutdown
  Instrument loop diagram for GTG confirmed incomplete termination of configured signal loop between HIMA SIS and GTG, hence failure of GTG to respond to ESD 2.5 signal (the Emergency stop relays (RLREMS 1&2) between Siemens SGT400(GTGs) emergency stop system (EMS) and Tyco F&G panel were incorrectly terminated with a resultant voltage source during the units’ TYCO F&G R4 upgrade in March 2020. Hence rendering the WD trip relay and SIS redundant from the Emergency stop system)
  Instrument loop diagram for AG turbines confirmed termination of configured signal loop between HIMA SIS and AG was unchanged, hence response of AG to ESD 2.5 trip

## Slide 7: Recommendations
  GAS DETECTION
  Identify and arrest sources of fugitive emissions around the plant.
  Carry out a campaign across the facility to connect the earthing cable for the OPGDs to the earth pit
  Implement voting for executive actions of all OPGDs in the plant. (Refer to Fire and Gas detection philosophy and follow voting logic specified in Section 5.7, page 14, Document no GEN-E15811-H02-00041)
  GTG FAILURE TO TRIP
  Implement permanent fix for Tyco Fire & Gas Emergency Shutdown System as scheduled for Q1 2021

## Slide 8
Harry Ariyo EPST Lead, Onshore
Uju Okwuosa EPST member
Viya Fariku EPST member
Joseph Zimughan Maintenance TL, Gbaran
Investigation Team