## FS Cadence
L1……….L2…..…..L3…….…..L4…..…...L5
| S/No. | ISSUE | JUSTIFICATION | % Occurrence | RCA STATUS | TIMELINE FOR EXECUTION/ACTION PARTY |  |  | COST OF EXECUTION ($) | STATUS
INSTALLATION & COMMISSIONING OF SOKU F/S UPS SYSTEM
|  | ISSUE | JUSTIFICATION |  |  | START DATE | END DATE | ACTION PARTY
HELP REQUIRED | 1 | Secure budget for activity execution | Required for funding of the project |  | No | 29.12.2017 | 24.01.2018 | Adebisi/Terfa | DIY
SHORT TERM | 1 | Scope the collapsed battery room floor and battery rack. | Required to outline activities to be carried out, and the funds required for work execution |  | No | 08.11.2017 | 27.12.2017 | Nwokorie Celestine | Nil | Done
| 2 | Engage asset engineering in a cost Review/challenge session | cost optimization and value assurance |  | No | 14.12.2017 | 29.12.2017 | Aminu Sani/Festus Azibator | Nil | Cost challenge session on-going
| 3 | Cut out, replace damaged structural members and install checkered plates as new floor | Strong and reinforced floor is required to withstand the weight of the batteries. |  | No | 26.02.2018 | 12.03.2018 | Nwokorie Celestine | 26487.1293 | Dedicated supervison is key. agreed design is checkered plates.
| 4 | Fabricate new battery racks. | To enable firm support of the batteries. |  | No | 26.02.2018 | 16.03.2018 | Nwokorie Celestine
| 5 | Repair broken door hinges | To secure equipment in the room |  | No | 19.03.2018 | 21.03.2018 | Nwokorie Celestine | Nil
| 6 | Position & install the batteries on the rack. | For proper arrangement of the batteries and terminations/connections. |  | No | 25.03.2018 | 02.04.2018 | Aminu Sani/Festus Azibator | DIY | Commencement date: 25.03.2018. This will commence after reinforcement of the floor and fabrication of the racks.
| 7 | Connect installed batteries to 30KVA AEG UPS unit | This is required to link the batteries to the UPS. |  | No | 03.04.2018 | 06.04.2018 | Aminu Sani/Festus Azibator | DIY | Commencement date: 03.04.2018. This will commence after the installation of the batteries.
| 8 | Hook-up UPS assembly to LV switchboard. | To convey power form LVSB to UPS for necessary battery charging. |  | No | 09.04.2018 | 11.04.2018 | Aminu Sani/Festus Azibator | DIY | Commencement date: 09.04.2018.
| 9 | Pre-commission/commission and conduct 72 hours reliability test | To ensure the correctness of all connections, proper functionality of all sub-units and overall performance of the entire UPS system etc. |  | No | 16.04.2018 | 25.04.2018 | Aminu Sani/Festus Azibator | DIY | Commencement date: 16.04.2018.
26487.1293