## Slide 1: IMO RIVER GAS LIFT HEALTH CHECK WORKSHOP

## Slide 2: AGENDA

## Slide 3: WORKSHOP OBJECTIVE
Carryout a Health Check of Imo River Gaslift system
Share a common understanding on the Status of :
    Surface/Subsurface Facilities (Physical Asset)
    Data Requirements/Gaps.
    Decisions/Plans
    Execution Capability
    Gas lift Surveillance Process
Distil big ticket items that will impact on the bottom line
Develop a roadmap to address the identified issues
Size of the Prize

## Slide 4: Workshop Deliverables
Completed Health Check Template
Big ticket items: Impact of technical issues
Road Map to Closeout Identified key areas of improvement with clear accountabilities
Size of the Prize (Deferment reduction, New Opportunities, Optimization etc.)
Imo river Gas Lift Improvement Plan

## Slide 5: Rules of the Game
Open discussion
KISS (Keep It Short and Simple)
Respect for all
Take technically detailed discussions ”offline” for further consideration
Own the Plan

## Slide 6: IMO RIVER GASLIFT SYSTEM PERFORMANCE
Setting the Scene
1.0

## Slide 7: Imo River Field Summary
Location: 30km NE of PH
Disc/Onstream: 1959/61
Wells to date: 66 (5 aband.)
STOIIP/UR (MMstb) : 1677/1013 ??
Np @ 30.04.2017(MMstb): 692 ??
Cur Prod (Mbopd) : 16.5
3D Seismic: 1990/2003
FDP: 1997
Reservoir: 34(22)
Depth in ftss: 5000 – 11000

## Slide 8: Imo River Production Performance
Civil war
Peak - 109Mpd
Drilling campaign after 3D seismic
HZ wells drilling campaign – 10 new wells
Increased WRM efforts

## Slide 9: IMOR 2017 GL Well Stock Status: 2015-2017

## Slide 10: Production: IMOR GAS LIFT SYSTEM SURFACE REVIEW
Current Realities
    Deferment as @ End Jan 2018 -1.1Mbopd (0.3 Mbopd GL related)
    Poor FLM coverage for Gaslift Distribution manifold.
    Limited Lift gas Metering, control capability, and manual optimization
    Improved deferment management of quit wells portfolio . Deferred wells portfolio??
    Standardised process for opportunity Identification, maturation and trouble shooting in place but compliance an issue. Perhaps there is scope for optimisation
    Sub optimal well designs and legacy completion strategy.
    Limited collaboration and slow restoration of deferred wells.
    Poor/Reactive Surveillance (Surface & Subsurface).
    Improved Compressor uptime > 75% in Imor PU.

## Slide 11: IMO RIVER GAS LIFT WELLS DEFERMENT PROFILE
Chart: 2017 to Jan 2018 IMOR GL deferments
| Wellhead Equipment | Pipeline | Deliveryline/Trunkline | Flowline | AG Compressor | Subsurf Safety Valve | Facility Equipment Trips | Manifold | Reservior | Gaslift Valve | Flowline Safety Valve
'17 to Date GL deferments | 537874.7704 | 210763.1514 | 192377.4082 | 28891.6902 | 31722.5212 | 18508.5114 | 20305.3465 | 5747.0336 | 2052.2796 | 1693.908 | 61.1257
Oil (bbl) | Gas (scf) | Reason
537,875 | 307,916 | Wellhead Equipment
210,763 | 65,651 | Pipeline
192,377 | 58,785 | Deliveryline/Trunkline
28,892 | 17,890 | Flowline
31,723 | 12,171 | AG Compressor
18,509 | 7,306 | Subsurf Safety Valve
20,305 | 7,044 | Facility Equipment Trips
5,747 | 4,632 | Manifold
2,052 | 794 | Reservior
1,694 | 678 | Gaslift Valve
61 | 17 | Flowline Safety Valve

## Slide 12: Production: IMOR GAS LIFT SYSTEM SURFACE REVIEW
Identified data quality issues
  No Lift gas measurements during GL wells routine tests (need to leverage on Agbada example)
  Bulk gas lift metering issues: Instantaneous reading not seen, except over 24hrs.
Identified facility/process Integrity issues
  vandalized well-heads, foaming and waxy wells.
  Deferment Analysis: Wells, Gas lift sharing issues in wells, Gas lift valves in hole beyond cycle life of 2years. All GL wells in Imor have valves in hole without change out for over 6 years (impacted by scaling issues in tubing)
Reviewed AGG performance issues:
  Critical spares availability, Power supply and operational issues.
Security: Third party interference IC’s etc) , Improvement of security around wellheads & flowlines
Identified Surface field Hardware issues
  No MJR for the Gas lift manifold, hence no PM triggers from SAP; Low TEG unit uptime, hence liquid ingress into the GL manifold; Some FCVs in manual mode

## Slide 13: Production: IMO RIVER GAS LIFT VALVES IN HOLE REVIEW

## Slide 14: GAS LIFT SURVEILLANCE PROCESS
Convince
management
Create GL
Team
Analyze
Wells
GL Champion
Re-design/re-distribute
Spot
Problems
Implement
Changes
Improve
Data & Systems
Field PTs, Gas Lift Team
Field Techs, Well Analysts
Shell’s Surveillance Strategy:
Support
Process
Model
Performance

## Slide 15: GAS LIFT SURVEILLANCE PROCESS
Role of Field Technicians/Well Analysts is to be the eyes, ears
and hands of the PTs and GL champions by:
Spotting problems (e.g. heading, low production)
Implementing and monitoring changes
Improving data
Monitoring and operating control systems
Improving implementation of the process
Well heading
severely. I will
increase gas
and you
redesign it.
Field Technicians & Well
Analysts

## Slide 16: GAS LIFT SURVEILLANCE PROCESS
Role of Field PTs/Gas Lift Team is to manage the process by:
Analyzing and modeling the wells
Re-designing as necessary
Optimizing compressor utilization
Training the Field Technicians/Well Analysts
Maintaining the data
Keeping cost/benefits indicators
Co-ordinating wireline operations
Estimated
lift depth
8630’. A 150
bbl/d increase
expected.

## Slide 17: GAS LIFT SURVEILLANCE PROCESS
Since gas lift can quietly get inefficient, gas lift surveillance should be proactive. Don’t wait until a well goes off production. Review each well plus the system itself several times a year.
Since there are no mechanical connections to the lift system in the well, spend time and money to gather quality information on the performance of each well. The proper use of this information will find inefficiencies and make money.
Industry examples (in and out of Shell) show the systematic optimizing of gas lift operations produce 5-15% gains in oil production at little cost -- the lowest cost per barrel of any oil in a field.
Inefficiency continues without a process to combat it. Surveillance should be a process not a project.

## Slide 18: IMOR 2017 AGG AVAILABILITY/RELIABILITY PERFORMANCE 2017
Setting the Scene
1.4

## Slide 19: AGG Availability: 2017 Performance
Chart: Controlled Availability (%)
| 42736 | 42767 | 42795 | 42826 | 42856 | 42887 | 42917 | 42948 | 42979 | 43009 | 43040
Availability (%) | 66.8 | 100 | 100 | 24.21 | 100 | 100 | 100 | 100 | 82.14 | 55.1 | 80.8
82% RUNNING AVERAGE

## Slide 20: AGG Availability: 2017 Performance
Chart: AGG Bad Actors
| Frequency
Process/Spurious Alarms | 4
AGG Compressors | 3
Generator failures | 2
Lube oil pumps | 2
Turbine issues | 1
Lightning strike | 1
Instrument Air Compressor | 1
Bad Actors
Recurring AC/DC Lube oil pump failures
Gas Gen failures
Instrument Air compressor failure
High Level 1st stage suction scrubber/ turbine fuel valve failed (Jan 17)
Lightning strike (May 17)
Compressor dry gas seal failure (Oct /Nov17)

## Slide 21: Imor PU Gas-Lift Health Check – Results (SAMPLE)
Kick-off gaslift in Imor field
Gas lift valves and GL lines installation plans
Integrated Asset Activity Plan available
Real time systems implementation plan
Winglue modelling course readily available for PT’s
Automated gaslift system plan in place
Plan & process in place to build WinGlue models
CAO SCADA plan in place
Procurement & Storage of parts and materials.
Updated Asset Reference Plan
Maintained focus on the corporate WRM initiative
Optimization/rationalization strategy for GL
Lift gas metering for individual wells.
Winglue training for PT
Kick off astanding gas lift in wells with mandrels
Planning and selection of data acquisition candidates
Determine the size of the prize (impact of gas lift in the Asset)
Ranked list of opportunities
Real time acquisition of production data
Gaslift training for operations, maintenance and PTs
Contractors for GL optimisation
Competent hand within CWI, O&M Contractor + Operations
Good Dev - Well Services interface
Good Operations-Development interface
Installation of GLV, unloading and kick-off of wells with/without mandrels.
Compressor station availability/uptime at 95% ok
Manning level and lack of staff continuity in gaslift system operations.
Critical spares and sustainable procurement of parts for the IGPES compressor/gas plants
GL competence and staff motivation
Competencies in gaslift optimisation.
Availability of Well services barge
Security situation impacting on operations
Silted slots
Gas lift lines availability (Some lines required to be replaced)
Inability to run the two compressors the same time
Gas break-in/Foam in SV creating pump cavitation and low production
CAO SCADA unavailability hampering real time monitoring / Well testing
No updated gaslift system operating envelop for optimisation
BHP surveys ( SG) done regularly.
Gauges are regularly calibrated
Test separator availability
Data gathering plan in place
USM available in flowstations.
Metering & Production allocation
Time lag btw sample acquisition and analysis at the lab & prod. Prog.
Concurrent well test not always done with sampling & BHP acquisition. GOR measurement suspect
CAO SCADA not available Real Time BS&W
BSW probes not available on test separators
No Capability for real Real time data capture and analysis
EC available and in use (welltest data)
Availability of up-to-date well status diagram
Availability of temperature data.
Accuracy of data in the corporate BHP database
Quality of BSW data
Wellhead Pressure data (feedback not regular)
Injected Gas, measurement and optimisation
Competent PTs for building WinGLUE models
Competence in analyzing BHP surveys
Skills development
  Programming & operations
  Winglue
  Field ware etc
Real-time monitoring of gaslifted wells
PROSPER models available
Winglue models.
UNISIM Models available for the flowstation
Gap model available.
MBAL available
IPSM available
Gaslift manifold in place (planned to maintain FCVsr)
xx MMscfd of gas(HP)) available for gaslift compression
Lift gas metering on individual wells available
Adequate no of pumps
Gaslift lines to wells in place; some leaking gaslines.
Vmonitor/CAO/SCADA not functional.
Gas metering Facility(No integrators)
Optimization of dual string completion.
Gaslift manifold desanding to prevent wet gas injection to the wells.

## Slide 22: IMO RIVER 2018 Targets
Where We Want to Be
2.0

## Slide 23: IMO RIVER PU PRODUCTION BATTLE PLAN
Source: ImoR PU strategy workshop, Wells potential BI rates and WRFM 2018

## Slide 24: IPSC GROWTH PLAN AND ENABLERS
Source: ImoR PU strategy workshop, Wells potential BI rates and WRFM 2018
Chart: IMOR Production Unit 2018 IPSC Growth Strategy
| IMOR Avail. IPSC Wells ( Jan 11, 2018) | Isimiri FS RSP. Repairs | CWI interventions (22S, 32S, Nkal 13L/S) | 36L/S STOG REST ongoing | OP 17 STOG Wells (2T, 5S, 13L/S, 18L, 30L, 44S, 57L) | OP 17 Planned STOG OPZ (Isim 1S, Nkal 4L/S) | OP 17 Planned STOG REST (ImoR36L/S, 60T, 66T, 33L, 44L, 48L/S, 51L, 56L/S) ) | Additonal non AF DNL_CIWR Wells (ImoR 29L/S, 39T, 4T, Nkal 2L/s, Nkal 5L/S, Nkal 9L/S, Nkal 11L/S, 11V, Nkal 14L/S) | 1kbopd Tgt set for each of the 4 Quarterly PSOs | Imo R PU Potential IPSC
 | 15.6 | 15.6 | 16.61 | 17.28 | 17.88 | 19.78 | 20.78 | 23.08 | 28.98 | 32.98
 | 0 | 1.01 | 0.67 | 0.6 | 1.9 | 1 | 2.3 | 5.9 | 4 | 0
 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Slide 26: Opportunity/Risk Identification
Project : _____________ Team : _________________
Rank (H/M/L) | Opportunity | Comments
Rank (H/M/L) | Risk | Mitigations

## Slide 27: SWOT Analysis
Build on STRENGTHS | Exploit OPPORTUNITIES
Resolve WEAKNESSES | Avoid THREATS

## Slide 28: Idea Mapping
Project : _____________ Team : _________________
Easy implementation
Challenging implementation
High value
Low value

## Slide 29: Action Planning
Project : _________________ Team : _________________
ID | Idea / Opportunity | Action ID | Action | Responsible Party | Start Date | End Date | Comments