## Deliverables
PU | Process Steps | Activity | Action Lead | Pillars | Deliverables | Equipment | Weight | Close out Date | % Completion | Comment | Comment Date
Gbaran | MSC/TA/ME | AGC blow down valve failure / Passing Valves / Maintenance on boundary valves Stem protected against weather to avoid water and dirt build-up causing corrosion/erosion | Amuno Odiri / Nkere Chidiebere | Maintenance & Operations | Condition check (cleanliness/condition) of proximity switches covered by Operator Round FLM or task captured in PM task list. |  | 1 | 2023-06-30 | 40% | 28/07 Amuno/Itoro to create Z6 and include in MJR task list. 26/09/23: Amuno/Itoro to create Z6 and include in MJR task list (delegate to Ashaka) - 4/10/2023 20/10/23 Helen to raise z6 before 27/10/23
Gbaran | MSC/TA/ME | AGC Seal Gas Issues All instrumentation on Seal gas Systems correct design (range) and in good condition | Amuno Odiri / Nkere Chidiebere | Maintenance & Operations | Obtain an approved MoC for the proposed changes in instrumentations on the seal gas system. |  | 1 | 2023-03-31 | 0% | 26/09/23: Clarify with Kene
Gbaran | MSC/TA/ME | AGC Seal Gas Issues All instrumentation on Seal gas Systems correct design (range) and in good condition | Amuno Odiri / Nkere Chidiebere | Maintenance & Operations | Obtain Specification of new modified instrumentation and place an order for procurement. |  | 1 | 2023-06-30 | 60% | Some transmitters are on order. Get PO from AGG Team 26/09/23: Clarify with Kene
Gbaran | MSC/TA/ME | AGC Seal Gas Issues All instrumentation on Seal gas Systems correct design (range) and in good condition | Amuno Odiri / Nkere Chidiebere | Maintenance & Operations | Raise Notifications for the changes in instrumentations. |  | 1 | 2023-03-31 | 70% | 26/09/23: Clarify with Kene
Gbaran | MSC/TA/ME | AGC Seal Gas Issues All instrumentation on Seal gas Systems correct design (range) and in good condition | Amuno Odiri / Nkere Chidiebere | Maintenance & Operations | List instrumentation that needs modification |  | 1 | 2023-03-31 | 70% | Faulty instrumentation in the Seal Gas systems have been identified. 26/09/23: Clarify with Kene
Gbaran | MSC/TA/ME | AGC Seal Gas Issues All instrumentation on Seal gas Systems correct design (range) and in good condition | Kene Odunze | Maintenance & Operations | Review condition of all instrumentations on the Seal gas Systems |  | 1 | 2023-03-31 | 80% | Generall checks on the Seal Gas system has been carried out. Corrective actions to be incorporated during the AGC1 engine changeout. 26/09/23: Clarify with Kene
Gbaran | MSC/TA/ME | AGC Seal Gas Issues All instrumentation on Seal gas Systems correct design (range) and in good condition | Amuno Odiri / Nkere Chidiebere | Maintenance & Operations | List instrumentation that needs 1:1 replacement on the Seal gas systems. |  | 1 | 2023-03-31 | 80% | 26/09/23: Clarify with Kene
Gbaran | MSC/TA/ME | AGC Seal Gas Issues Seal gas flow transmitters operating in range (ability to re-calibrate in range) | Amuno Odiri / Nkere Chidiebere | Maintenance & Operations | Installation and commissioning of the new transmitters |  | 1 | 2023-05-31 | 0% | 26/09/23: Revert to Kene
Gbaran | MSC/TA/ME | Gas Turbine Air Flow Switches Upgraded Flow Switch installed and commissioned | Amuno Odiri / Nkere Chidiebere/Kene Odunze | Maintenance & Operations | Get approval for Asset Budget |  | 1 | 2023-03-04 | 100% | 28/04/23... get into the CAPEX build... 26/09/23: Share PO number. Amuno (04/10/23) Kene engaging the vendor to update the commercial qupte 26/04/2024: To be captured in OP24 10/05/2024: PO Number 4510505134
Gbaran | MSC/TA/ME | AGC Seal Gas Issues Seal gas flow transmitters operating in range (ability to re-calibrate in range) | Amuno Odiri / Nkere Chidiebere | Spares | Expedite delivery of new transmitters (Q1-23) |  | 1 | 2023-05-31 | 60% | 28/04/23. transmitters have been ordered, lets know the status. 26/09/23: Revert to Kene 20/10/23: Uju to follow up with Kene 2/5/24: AGG to share PO for ordered transmitters
Gbaran | MSC/TA/ME | Alternators – Preventive Maintenance not planned for and not executed | Kpoudosu David/ Emetubelem Muolee | Maintenance & Operations | Carry out Alternators A/B/C OEM-recommended Milestone inspections which are overdue |  | 1 | 2023-07-30 | 5% | 07/07/2023: Quotation sent by OEM. Revised quote needed. 26/09/23 :Secure TA's approval of this activity. 20/10/23: Abdul to align with TL and TA by 30/10/2023
Gbaran | MSC/TA/ME | Competence Enhancement / Capability Management Competence Management Plan in place and actioned | Kene Odunze/Romeo | Capabilities | Embed Sustainable: Include in Competence Management Framework, and keep it evergreen. For both Ops and Mtc |  | 1 | 2023-04-30 | 20%
Gbaran | MSC/TA/ME | Competence Enhancement / Capability Management Competence Management Plan in place and actioned | Kene Odunze/Romeo | Capabilities | Mgt Plan for wider scope: including compressors and other key equipment (both PACO and Mechanical) Info: on mechanical Mtc operations: generally no gaps, but: 1 Gap exists for for Dry Gas Seals, training needed |  | 1 | 2023-04-30 | 30%
Gbaran | MSC/TA/ME | Competence Enhancement / Capability Management Competence Management Plan in place and actioned | Kene Odunze/Romeo | Capabilities | Develop Capability Mgt Plan that addresses the progressing/movement of personnel and make sure multiple persons are training (backup) Gaps: Applies mainly for Mtc |  | 1 | 2023-04-30 | 60% | Kene is working on the Capability Management Plan.
Gbaran | MSC/TA/ME | Gas Turbine Air Flow Switches Current (old type spring): timely change out and sufficient spares available to do so | Amuno Odiri / Nkere Chidiebere/Kene Odunze | Maintenance & Operations | Place Order for replacement of air flow switches. |  | 1 | 2023-03-31 | 100% | Order placed for new Air Flow Switches 26/09/23: Share PO number. Amuno (04/10/23) 10/05/2024: PO Number 4510505134
Gbaran | MSC/TA/ME | Competence Enhancement / Capability Management Competence Management Plan in place and actioned | Kene Odunze/Romeo | Capabilities | Clarify on activity that will be conducted by Asset Team Then: Definition of Competence Needed |  | 1 | 2023-04-30 | 70% | Update the RACI list
Gbaran | MSC/TA/ME | Competence Enhancement / Capability Management SGT 400 Control System: Local team members trained on Control System | Kene Odunze/Romeo | Capabilities | Key Gaps: 1) Control: SGT400 Control System 2) Mech Mtc: Compressor DGS change out |  | 1 | 2023-03-31 | 30%
Gbaran | MSC/TA/ME | Gas Turbine Air Flow Switches Current (old type spring): timely change out and sufficient spares available to do so | Amuno Odiri / Nkere Chidiebere/Kene Odunze | Maintenance & Operations | Expedite and follow up for delivery of switches |  | 1 | 2023-03-31 | 50% | 26/09/23: Share PO number. Amuno (04/10/23) 10/05/2024: PO Number 4510505134
Gbaran | MSC/TA/ME | Gas Turbine Air Flow Switches Current (old type spring): timely change out and sufficient spares available to do so | Amuno Odiri / Nkere Chidiebere/Kene Odunze | Maintenance & Operations | Set and provide spares needed until upgraded flow switch is installed |  | 1 | 2023-04-30 | 40% | Air flow switches on order 26/09/23: Share PO number. Amuno (04/10/2023) 20/10/23: Charles to ask Nkere to raise PR to order some needed
Gbaran | MSC/TA/ME | Gas Turbine Air Flow Switches Current (old type spring): timely change out and sufficient spares available to do so | Amuno Odiri / Nkere Chidiebere/Kene Odunze | Maintenance & Operations | Set spares needed until upgraded flow switch is installed |  | 1 | 2023-03-31 | 60% | 26/09/23: Share PO number. Amuno (04/10/23) 10/05/2024: PO Number 4510505134
Gbaran | MSC/TA/ME | Gas Turbine Air Flow Switches Current (old type spring): timely change out and sufficient spares available to do so | Amuno Odiri / Nkere Chidiebere/Kene Odunze | Maintenance & Operations | Create a new Maintenance Plan for replacement of air flow switches with frequency |  | 1 | 2023-07-31 | 70% | 28/04/23 Mtce strategy is replace when bad. we are moving to transmitter type.Odiri to confirm this is workable with Ekeleme 26/09/23: Replace when switches on order are delivered
Gbaran | MSC/TA/ME | Gas Turbine Air Flow Switches Upgraded Flow Switch installed and commissioned | Amuno Odiri / Nkere Chidiebere/Kene Odunze | Maintenance & Operations | Raise and approved MoC for Upgraded Flow Switch (as per Siemens recommendation) |  | 1 | 2023-03-28 | 0% | 26/09/23: Share PO number. Amuno (04/10/23)
Gbaran | MSC/TA/ME | Gas Turbine Air Flow Switches Upgraded Flow Switch installed and commissioned | Amuno Odiri / Nkere Chidiebere/Kene Odunze | Maintenance & Operations | Update BoM and Coding in CMMS |  | 1 | 2023-03-01 | 0% | 26/09/23: Share PO number. Amuno (04/10/23)
Gbaran | MSC/TA/ME | Gas Turbine Air Flow Switches Upgraded Flow Switch installed and commissioned | Amuno Odiri / Nkere Chidiebere/Kene Odunze | Maintenance & Operations | Raise Notification/ Work Order for upgrade, installation and commissioning |  | 1 | 2023-05-05 | 0% | 26/09/23: Share PO number. Amuno (04/10/23)
Gbaran | MTO | Instrument Air Compressors – Freeze Common HMI Manage Reliability Existing HMI (until new HMI installed) | Uju Okwuosa/Richard | Maintenance & Operations | HMI: Once root cause(s) are confirmed, corrective actions to be defined and captured in MTO for tracking. |  | 1 | 2023-06-30 | 50% | Vendor report obtained. Obsolescence issues identified. Budget request raised for OP23 . Confirm we have this threat captured in Fit4?? 26/09/23: Share MTO ID -Nelson 20/10/23: Upgrade not supported in OP23, Gloria to pick up... 10/05/24: Maintenance Execution (Collins) to provide execution plan
Gbaran | System Selection And Scope | Resource the IVD plan | Kebin Ofori |  | Engage the task owners to conform resources needed and readiness to deliver |  | 1 | 2022-09-30 | 100%
Gbaran | System Selection And Scope | Identify Improvement Goal | Casmir Ojobor |  | Outline clear targets |  | 1 | 2022-09-30 | 100%
Gbaran | System Selection And Scope | Kick Off meeting stakeholders | Uju Okwuosa |  | Engage AGG team on IVD |  | 1 | 2022-09-30 | 100%
Gbaran | System Selection And Scope | Kick Off meeting stakeholders | Uju Okwuosa |  | Engage PS LT on IVD plans |  | 1 | 2022-09-30 | 100%
Gbaran | System Selection And Scope | Kick Off meeting stakeholders | Uju Okwuosa |  | Engage Asset Manager IVD plans |  | 1 | 2022-09-30 | 100%
Gbaran | System Selection And Scope | Kick Off meeting stakeholders | Uju Okwuosa |  | Name System Owners on IVD plans |  | 1 | 2022-09-30 | 100%
Gbaran | System Selection And Scope | Kick Off meeting stakeholders | Uju Okwuosa |  | Agree Cadence, DRB and Success measures |  | 1 | 2022-09-30 | 100%
Gbaran | MTO | Identify Threats on Fit4MTO database | Uju Okwuosa | Maintenance & Operations | Download threats and actions on MTO with impact on system |  | 1 | 2022-09-30 | 100%
Gbaran | MTO | Identify Threats on Fit4MTO database | Uju Okwuosa | Maintenance & Operations | Analyse data and identify threats with deferment, flaring impact, equipment with low availability |  | 1 | 2022-09-30 | 100%
Gbaran | MTO | Identify Bad actors (Review past trips and RCAs) | Uju Okwuosa | Maintenance & Operations | Review historical trip logs |  | 1 | 2022-09-30 | 100%
Gbaran | MTO | Identify Bad actors (Review past trips and RCAs) | Uju Okwuosa | Maintenance & Operations | Identify causes of trips |  | 1 | 2022-09-30 | 100%
Gbaran | MTO | Identify Bad actors (Review past trips and RCAs) | Uju Okwuosa | Maintenance & Operations | Review completed RCAs from past events |  | 1 | 2022-09-30 | 100%
Gbaran | MTO | Identify Bad actors (Review past trips and RCAs) | Uju Okwuosa | Maintenance & Operations | Download and review failure history on SAP |  | 1 | 2022-09-30 | 100%
Gbaran | MTO | Identify Bad actors (Review past trips and RCAs) | Uju Okwuosa | Maintenance & Operations | Enumerate common themes |  | 1 | 2022-09-30 | 100%
Gbaran | MSC/TA/ME | AGC blow down valve failure / Passing Valves / Maintenance on boundary valves Blown down valve not passing | Bosini Oghenevwogaga /Charles Ogbuehi | Maintenance & Operations | Confirm there is an active PM program for leak testing; greasing; stroke testing during plant down time |  | 1 | 2023-04-30 | 100% | 28/04/2023 we have these. greasing done in service....to confirm leak testing is part of other activities . Confirm leak test done as PM
Gbaran | MSC/TA/ME | AGC blow down valve failure / Passing Valves / Maintenance on boundary valves. Blown down valve not passing | Bosini Oghenevwogaga /Charles Ogbuehi | Maintenance & Operations | ESD/BDV maintenance strategy to be defined across unit: including PM for Overhaul valve and ACP coverage for Ultimate Replacement (end of normal life) ; maintenance covered in PM |  | 1 | 2022-04-30 | 100% | 02/06/23 Obsolescence mgt plan for these to be developed starting next month as per TA commitment. Valve PMs are available - 1yrly function testing of the valve. Replacement is done on as-need basis.
Gbaran | MSC/TA/ME | AGC blow down valve failure / Passing Valves / Maintenance on boundary valves ESD.BDV’s are covered by SIL study (IPF/SIFpro) | Bosini Oghenevwogaga /Charles Ogbuehi | Maintenance & Operations | ESD/BDV maintenance SIL. Confirm for all ESD. BDV's. |  | 1 | 2023-04-30 | 100% | 02/06/23 Confirmed by site team.
Gbaran | MSC/TA/ME | AGC blow down valve failure / Passing Valves / Maintenance on boundary valves Start-up sequence of AGC compressor not interrupted because of malfunction proximity switch actuator BDV | IT Ekanem / Njoku Richard | Spares | Follow up for delivery of the new BDV (incl. actuator, solenoid and proximity switches) on order |  | 1 | 2023-03-30 | 100% | Delivered
Gbaran | MSC/TA/ME | AGC blow down valve failure / Passing Valves / Maintenance on boundary valves Start-up sequence of AGC compressor not interrupted because of malfunction proximity switch actuator BDV | IT Ekanem / Njoku Richard | Maintenance & Operations | Plan and carry out the installation of the new BDV; Reconfirm scope in the 2023 turnaround. |  | 1 | 2023-08-30 | 100% | 02/06/2023 One valve installed during the recent shutdown in May 2023. In scope for TAM 09/06/23 confirm how many more need to be replaced in turnaround and progress as such. 16/06 More valves still expected. No XXX 28/07The one outstanding valve is planned for installation in July.
Gbaran | MSC/TA/ME | AGC blow down valve failure / Passing Valves / Maintenance on boundary valves Actuator has sufficient torque to close the valve | IT Ekanem / Njoku Richard | Spares | Define options to prevent water ingress (i.e Chinese cap. actuator, solenoid and proximity switches) Order and Install. |  | 1 | 2023-11-30 | 100% | 26/09/23: Generate Po for procurement of chinese caps. 20/10/23 -materials purchased already (for 10 valves) fabrication to begin by 3rd nov. Abass working with Gbaran workshop 24/11/23: 1/3 completed. Expected completion 08/12/2023 01/12/23: Completed
Gbaran | MSC/TA/ME | AGC Seal Gas Issues New seal gas heater avoids condensation of liquids which block up filter | Kene Odunze/Abaass Kabir/Agabi Lawson | Spares | Expedite delivery of new seal gas heater (Q1-23) for AGC1 |  | 1 | 2023-03-31 | 100% | 28/04/23 New seal Gas Heater installed.
Gbaran | MSC/TA/ME | AGC Seal Gas Issues New seal gas heater avoids condensation of liquids which block up filter | Solomon/Abass/Lawson/Chiemezie | Maintenance & Operations | Installation and commissioning of the new seal gas heater for AGC1 |  | 1 | 2023-05-31 | 100% | 28/04/23 New seal Gas Heater installed. Confirm Performance.
Gbaran | MSC/TA/ME | AGC Seal Gas Issues Seal gas liquids drain continuous in open position when in operation (continuous drain) | Akinlolu Haruna/Ibrahim Saheed/Solomon/Abass | Maintenance & Operations | Check operator round (FLM) scope for seal gas filter drain valve in open position and add if necessary |  | 1 | 2023-05-31 | 100% | 28/04/2023 Mech to check with operations team to agree on right position of valve 12/05/23 Should be open according to P&ID. Ops confirmed valves to be in open position. Saheed's mail.
Gbaran | MSC/TA/ME | AGC Seal Gas Issues Seal gas liquids drain continuous in open position when in operation (continuous drain) | Akinlolu Haruna/Ibrahim Saheed/Solomon/Abass | Maintenance & Operations | Consider making valve locked open, risk assses and pursue change through MoC |  | 1 | 2023-05-31 | 100% | 12/05/23 MOC might not be required as a cascade with operations team will suffice. Confirmed Valve as Normally Open Valve. Saheed's Mail
Gbaran | MSC/TA/ME | Instrument Air Compressors – Freeze Common HMI Manage Reliability Existing HMI (until new HMI installed) | Uju Okwuosa/Richard | Spares | Conduct structured Investigation into issues with IA compressors (HMI freezes in 2022), to understand and confirm the causes for the problems |  | 1 | 2023-06-30 | 100% | RCA Completed
Gbaran | MTO | Instrument Air Compressors – Freeze Common HMI Info: issues in 2012-2020 related to OPC server 2020: OPC server upgraded to PK controller, reduced problems. | Uju Okwuosa/ Abdul | Maintenance & Operations | Investigate Electric Motor failures (2020). 1st replaced, 2nd about to be replaced. Main root cause yet to be confirmed (lubrication or other?) |  | 1 | 2023-06-30 | 100% | 24/03/23 ; decide on date to start RCA on electric motor failure RCA Completed. Root Cause was wrong selection of Bearings and Grease.
Gbaran | MTO | Instrument Air Compressors – Freeze Common HMI Info: issues in 2012-2020 related to OPC server 2020: OPC server upgraded to PK controller, reduced problems. | Uju Okwuosa | Maintenance & Operations | Electric Motors: Once root cause(s) are confirmed, Define corrective actions and track to closure using MTO |  | 1 | 2023-07-03 | 100% | Corrective Actions identified. The correct bearings and grease identified for future activities. The failed electric motor has been repaired. Post RCA coompletion.
Gbaran | MSC/TA/ME | Fire & Gas Detection Issues #1 Accelerate the delivery of alignment piece (on order) | IT Ekanem / Njoku Richard | Maintenance & Operations | Confirm spec for the alignment piece (information to order the piece) – new model |  | 1 | 2023-01-15 | 100%
Gbaran | MSC/TA/ME | Fire & Gas Detection Issues #1 Accelerate the delivery of alignment piece (on order) | IT Ekanem / Njoku Richard | Maintenance & Operations | New model included in SAP (CMMS) – coding - DONE |  | 1 | 2023-01-15 | 100%
Gbaran | MSC/TA/ME | Fire & Gas Detection Issues #1 Accelerate the delivery of alignment piece (on order) | IT Ekanem / Njoku Richard | Maintenance & Operations | Make Requisition for alignment tool DONE |  | 1 | 2023-01-15 | 100%
Gbaran | MSC/TA/ME | Fire & Gas Detection Issues #1 Accelerate the delivery of alignment piece (on order) | IT Ekanem / Njoku Richard | Spares | Engage C&P team to expedite delivery (no issues with funding at the moment) |  | 1 | 2023-03-15 | 100% | Alignment kit delivered at site
Gbaran | MSC/TA/ME | Fire & Gas Detection Issues #1 Accelerate the delivery of alignment piece (on order) | IT Ekanem / Njoku Richard | Maintenance & Operations | Demonstration on use of new model of alignment kit 1) study the manual and 2) do a demonstration to the rest of the mtc team |  | 1 | 2023-07-15 | 100% | Amuno carried out demonstration.
Gbaran | MSC/TA/ME | Fire & Gas Detection Issues #2 Maintenance frequency to clean lenses and further campaign/preventive maintenance, including MJR | Uju Okwuosa | Maintenance & Operations | Review Maintenance Strategy (freq) and scope (which detectors). Consider resource/ man power availability. Current 1Y, probably better 6M. Cleaning lenses maybe need more often (3M) but resource impact. RCM |  | 1 | 2023-06-30 | 100% | 24/03/23: F&G is for SIF studies, to contact Awe and decide on plan going forward 20/10/23:Engagements done, @Helen Miene to raise z6 also including action in 45 below
Gbaran | MSC/TA/ME | Fire & Gas Detection Issues #2 Maintenance frequency to clean lenses and further campaign/preventive maintenance, including MJR | Uju Okwuosa | Maintenance & Operations | MJR content: Improve existing and develop new MJR, including the work preparation (e.g. requirement for manlift, or scaffold etc). Note: cleaning of lenses is already included in MJR. Include in MJR all equipment in the loop like cabling, surge protection barrier etc. |  | 1 | 2023-06-30 | 100% | MJR with updated frequency has been impleted with z6.
Gbaran | MSC/TA/ME | Fire & Gas Detection Issues #2 Maintenance frequency to clean lenses and further campaign/preventive maintenance, including MJR | Uju Okwuosa | Maintenance & Operations | Check with Soku experience with F&G and adopt possible learnings. |  | 1 | 2023-06-30 | 100% | 20/10/23 This was also for frequent trips in condensate spiking. Implemented downgrade of executive action to OSD2 from ESD
Gbaran | MSC/TA/ME | Fire & Gas Detection Issues #3 Scope for the optical detector replacements (On the run or during TAM) | IT Ekanem / Njoku Richard | Maintenance & Operations | Obtain Spec/datasheet for new detector (:new gas detector already installed in new section, use this |  | 1 | 2023-05-30 | 100% | 07/07/2023: Replacement of detectors and upgrade of fire and gas system completed September 2022
Gbaran | MSC/TA/ME | Fire & Gas Detection Issues #3 Scope for the optical detector replacements (On the run or during TAM) | IT Ekanem / Njoku Richard | Maintenance & Operations | Start Simple (single discipline) MoC required, to capture documentation changes, Bill of Material and Coding and mods to fixing bracket and hangers Identify Flocs (info: between 50-100 total), also include remote locations |  | 1 | 2023-04-30 | 100% | 30/06/2023: Odiri to confirm from Itoro the status of this in terms of MOC et al + alignment piece 07/07/2023: Replacement of detectors and upgrade of fire and gas system completed September 2022. MoC not required as detectors were like for like.
Gbaran | MSC/TA/ME | Fire & Gas Detection Issues #3 Scope for the optical detector replacements (On the run or during TAM) | IT Ekanem / Njoku Richard | Maintenance & Operations | Update SAP info Follow normal mtc process: include Notification and do work preparation |  | 1 | 2023-06-30 | 100% | 07/07/2023: Replacement of detectors and upgrade of fire and gas system completed September 2022
Gbaran | MSC/TA/ME | Fire & Gas Detection Issues #3 Scope for the optical detector replacements (On the run or during TAM) | IT Ekanem / Njoku Richard | Maintenance & Operations | Replacement of gas detectors on the run by Mtc team. Gas Detectors removed: keep as spare. |  | 1 | 2023-08-30 | 100% | Not applicable as damaged detectors cannot be used as spare
Gbaran | MSC/TA/ME | Fire & Gas Detection Issues #3 Scope for the optical detector replacements (On the run or during TAM) | IT Ekanem / Njoku Richard | Maintenance & Operations | Point gas detector: obsolete, upgrade available. Phase out old detectors, order new once and install these |  | 1 | 2023-06-30 | 100% | 07/07/2023: Replacement of detectors and upgrade of fire and gas system completed September 2022. Like for like detectors used and detectors were repositioned in the turbine
Gbaran | MSC/TA/ME | Gas Turbine Air Flow Switches Current (old type spring): timely change out and sufficient spares available to do so | IT Ekanem/Njoku Richard/Kene Odunze | Maintenance & Operations | Confirm replacement frequency of air flow switches |  | 1 | 2023-03-31 | 100% | 28/04/23 Mtce strategy is replace when bad. we are moving to transmitter type.Odiri to confirm this is workable with Ekeleme
Gbaran | MSC/TA/ME | Gas Turbine Air Flow Switches Current (old type spring): timely change out and sufficient spares available to do so | IT Ekanem/Njoku Richard/Kene Odunze | Maintenance & Operations | Current overdue replacements: Raise notification and replace soonest |  | 1 | 2023-03-31 | 100% | Alll faulty air flow switches have been replaced.
Gbaran | MSC/TA/ME | Alternators – Preventive Maintenance not planned for and not executed RCM executed PM Tasks loaded in SAP MJR defined | Mohammed Abdul /Okolo Nelson/Uju Okwuosa | Maintenance & Operations | Refer to MTO Fit 4 Initiative #21: Review Gbaran Ubie Equipment Care Plans Existing Initiative action: Develop Maintenance Strategy for GTG |  | 1 | 2023-06-30 | 100% | 28/04/23 Charles to check for this 05/05/23 there is a 2 yrly plan for the alternators and this is on the CMMS 07/07/2023 Mtce plan is available on SAP
Gbaran | MSC/TA/ME | Alternators – Preventive Maintenance not planned for and not executed RCM executed PM Tasks loaded in SAP MJR defined | Mohammed Abdul/Okolo Nelson /Uju Okwuosa | Maintenance & Operations | Action shall include: Run RCM, develop MJRs, load into SAP and include in Asset Care Plan Note: SNEPCO / BONGA is conducting RCM for their alternators. |  | 1 | 2023-06-30 | 100% | 07/07/2023: ACP will build from existing mtce plans, MJR.. 26/09/23 : MPs available See MP's 100051082 100051110 100112194
Gbaran | MSC/TA/ME | GTG Alternators – Preventive Maintenance not planned for and not executed | Uju Okwuosa | Maintenance & Operations | Asset Care Plan to be developed, including references with Maintenance Reference Plan |  | 1 | 2024-06-30 | 100% | 24/03/23: Included in budget for OP '23. Changed close out date to 2024
Gbaran | MSC/TA/ME | Alternators – Preventive Maintenance not planned for and not executed | Kpoudosu David/ Emetubelem Muolee | Maintenance & Operations | Develop preservation procedures for equipment (alternator) in warehouse. |  | 1 | 2023-04-30 | 100% | Alternator was inspected in 2023. Yet to develop a procedure for the process. 26/09/23: Develop preservative maintenance plan for alternators. Nelson 04/10/2023. 20/10/23: Abdul to close out before 27/10/23 26/04/24: Presevation Procedure completed
Gbaran | MSC/TA/ME | Alternators – Preventive Maintenance not planned for and not executed | Mohammed Abdul/ Okolo Nelson | Maintenance & Operations | Full spare alternator in warehouse: condition unknown – to be inspected + updating preservation maintenance |  | 1 | 2023-04-30 | 100% | 05/05/23 Team to develop preservative care plan for this 07/07/2023: Inspection carried out. Awaiting report. 26/09/23: Alternator is okay
Gbaran | MSC/TA/ME | Obsolesence management incl IA Comp HMI, C2Link Obsolesence in place as per AMS: Integrated in ACP for critical equipment (e.g. DCS and Control Systems). (note: MRP as source) | Bosini Oghenevwogaga /Gloria Usiagu | Maintenance & Operations | 1) Proactive assessment on date when obsolescence is expected of systems/equipment (horizon: up to end of field life – Multiyear outlook) |  | 1 | 2023-06-30 | 100% | 28/04/23 vendor was on site last week...to look at obsolescence. Awaiting report post vendors visit for cost implication of upgrade 09/06/23 TA to visit in July for assessment 26/09/23: Charles to Share plan -shared
Gbaran | MSC/TA/ME | Obsolesence management incl IA Comp HMI, C2Link Obsolesence in place as per AMS: Integrated in ACP for critical equipment (e.g. DCS and Control Systems). (note: MRP as source) | Bosini Oghenevwogaga /Gloria Usiagu | Maintenance & Operations | Info: For Long Lead Items: reference is made to IVD sustain topics for Soku. (note: phased approach). |  | 1 | 2023-07-01 | 100% | Updated Obsolescence management plan signed off. To capture recommendations in the Fit4MTO Signed off
Gbaran | MSC/TA/ME | Obsolesence management incl IA Comp HMI, C2Link Obsolesence in place as per AMS: Integrated in ACP for critical equipment (e.g. DCS and Control Systems). (note: MRP as source) | Bosini Oghenevwogaga /Gloria Usiagu | Maintenance & Operations | Approach for long lead items and budget request to be embedded in work process/system, including R&R and annual key milestones |  | 1 | 2023-07-02 | 100% | Updated Obsolescence management plan signed off. To capture recommendations in the Fit4MTO
Gbaran | MSC/TA/ME | Obsolesence management incl IA Comp HMI, C2Link Budget approved and available in time | Bosini Oghenevwogaga /Gloria Usiagu |  | On Annual basis: Collect input from Asset team as scope for the Obsolesence plan |  | 1 | 2023-04-30 | 100% | Updated Obsolescence management plan signed off. To capture recommendations in the Fit4MTO
Gbaran | MSC/TA/ME | Obsolesence management incl IA Comp HMI, C2Link Budget approved and available in time | Bosini Oghenevwogaga /Gloria Usiagu | Maintenance & Operations | Specific for Gbaran Ubie: (Info Budget for 2023 has been closed) Action: for GU obsolescence scope (e.g. IA Comp HMI and C2Link): to be included timely for 2024 budget |  | 1 | 2023-04-30 | 100% | Updated Obsolescence management plan signed off. To capture recommendations in the Fit4MTO
Gbaran | MSC/TA/ME | Obsolesence management incl IA Comp HMI, C2Link ACP: annual update, also on Obsolesence management | Bosini Oghenevwogaga /Gloria Usiagu | Maintenance & Operations | Info: OP – 5 year outlook JV partners: request for annual budget AND provide outlook for multiyear budget. Include info on business impact of elements |  | 1 | 2023-07-31 | 100% | Updated Obsolescence management plan signed off. To capture recommendations in the Fit4MTO 20/10/23: Uju to ensure recommendations are captured on fit4
Gbaran | MSC/TA/ME | Obsolesence management incl IA Comp HMI, C2Link ACP: annual update, also on Obsolesence management | Bosini Oghenevwogaga /Gloria Usiagu | Maintenance & Operations | Specific for Gbaran Ubie: Explore possibility to tap into OPEX budget for 2023 |  | 1 | 2023-07-31 | 100% | 02/06/2023 TA to visit site in July for assessment Some Obsolescence items were handled during the 2023 TAM
Gbaran | MSC/TA/ME | Obsolesence management incl IA Comp HMI, C2Link Monitor, Track and Control implementation | Bosini Oghenevwogaga /Gloria Usiagu | Maintenance & Operations | Outcome to be aligned with input for 2024. |  | 1 | 2023-07-31 | 100% | OMP signed off
Gbaran | MSC/TA/ME | Export Pumps – Preventive Maintenance not planned for and not executed | Solomon/Abass/Lawson/Chiemezie | Maintenance & Operations | Refer to MTO Fit 4 Initiative #21: Review Gbaran Ubie Equipment Care Plans |  | 1 | 2023-07-31 | 100% | 28/04/23 Solomon to send mtce plan no as evidence of this availability
Gbaran | MSC/TA/ME | Export Pumps – Preventive Maintenance not planned for and not executed | Solomon/Abass/Lawson/Chiemezie | Maintenance & Operations | Include New Initiative action: Develop Maintenance Strategy / Plan for Export Pumps all Sub-Components. |  | 1 | 2023-07-31 | 100%
Gbaran | MSC/TA/ME | Export Pumps – Preventive Maintenance not planned for and not executed | Solomon/Abass/Lawson/Chiemezie | Maintenance & Operations | Action shall include: Run RCM, develop MJRs, load into SAP and include in Asset Care Plan |  | 1 | 2023-07-31 | 100%
Gbaran | MSC/TA/ME | GTG alternators – Preventive Maintenance not planned for and not executed RCM executed, PM Tasks loaded in SAP, MJR defined | Mohammed Abdul/Okolo Nelson | Maintenance & Operations | Alternator = Sub component Note: SNEPCO / BONGA is conducting RCM for their alternators |  | 1 | 2023-07-31 | 100% | Care Plans for the alternators exist and are active in CMMS
Gbaran | MSC/TA/ME | Competence Enhancement / Capability Management SGT 400 Control System: Local team members trained on Control System | Kene Odunze/Romeo | Capabilities | Identify current experts on SGT400 Control System in SPDC: not available, external support needed for upgraded control system |  | 1 | 2023-03-31 | 100% | Charles compiled the list and the areas of competence available
Gbaran | MSC/TA/ME | Competence Enhancement / Capability Management SGT 400 Control System: Local team members trained on Control System | Kene Odunze/Romeo | Capabilities | Engage with OEM to identify training material and trainer |  | 1 | 2023-03-31 | 100% | Training programmes are known
Gbaran | MSC/TA/ME | Competence Enhancement / Capability Management SGT 400 Control System: Local team members trained on Control System | Kene Odunze/Romeo | Capabilities | Compile Training Plan for SGT 400 and other critical equipment Note: recent control system upgrade (PLC system) |  | 1 | 2023-03-31 | 100% | 26/09/23: Romeo to engage Kene
Gbaran | MSC/TA/ME | Competence Enhancement / Capability Management SGT 400 Control System: Local team members trained on Control System | Kene Odunze/Romeo | Capabilities | Identify people that need to be trained |  | 1 | 2023-03-31 | 100% | Particpants nominated
Gbaran | MSC/TA/ME | Competence Enhancement / Capability Management Competence Management Plan in place and actioned | Kene Odunze/Romeo | Capabilities | Take action to Identify gaps in competence |  | 1 | 2023-04-30 | 100%

## Status
Completion Status
Completed
Ongoing
Not started

## Due Status
Due Status | Id
Overdue | 1
Due in 30 days | 2
Due 30 to 60 days | 3
Over 60 days | 4
Completed | 5

## System Owners
System Owner | PU
Didi Otobo | Tunu
Vincent Atey | Tunu
Chimuanya Onyejekwe | Soku
Musa Nabage | Soku
Abdul Mohammed | Gbaran
Charles Ogbuehi | Gbaran

## Pillars
Pillars
Maintenance & Operations
Spares
Proactive Technical Monitoring
Capabilities
Project to Asset

## PUs
PU | Title
Soku | SOKU INTEGRATED VALUE DELIVERY SUSTAIN
Tunu | INTEGRATED VALUE DELIVERY TUNU NODE COMPRESSOR AVAILABILITY
Gbaran | Gbaran Ubie – Sustaining the Gains from IVD Flaring Reduction Initiative

## Pivot
Row Labels | Count of % Completion
0% | 6
5% | 1
20% | 2
30% | 5
40% | 4
50% | 3
60% | 2
70% | 2
80% | 1
100% | 63
(blank)
Grand Total | 89