## Slide 1
SOKU INSTRUMENT AIR UPGRADE
Jan 2023
Increasing Equipment Reliability . Delivering Cost Savings
Project Charter

## Slide 2: Project Title: Soku Instrument Air System Upgrade
Over the last 5 years, Soku has spent ~$1,000,000 on it’s two AirPack Instrument Air System for a MTBF of 2 Weeks, an MTTR of 7 Days and materials lead time of >6 months, for comparison, within the same time frame, Gbaran has only spent ~$140k, a fraction of our cost, to maintain their 4 Atlas Copco Instrument Air System with MTBF of 100 Days and an available OEM in-country support. Soku can do better.
This initiative seeks to replace the existing two(2) reciprocating Air Pack Compressors (Installed in 1997 @740 Sm3/hr dry air & 10barg), with cheaper and easier-to-maintain screw type Atlas Copco Compressors capable of meeting the plant’s instrument and utility air requirements, yielding a savings of over $1M over 5 years.
Business Case
1
2
Management of Change request development and approval
Sizing of Atlas Copco air compressor based on instrument and utility air requirements at Soku GP .
Procurement and supply of Atlas Copco compressor and ancillaries
Execution at site and Commissioning
Challenges: Equipment selection risks - Selection of air compressors requiring minimal electrical work scope (To be tackled during opportunity framing)
Project Scope
3
Equipment Reliability: 700% Increase in Equipment Reliability.
Generating Shareholder Value: ~$1.0m cost savings over 5 years.
Achieving Net-Zero: Significant Reduction in GHG emissions and Noise Pollution. Enables Production of Lower Intensity Hydrocarbon.
Support: Availability of OEM presence and support in-country when required.
Potential Benefit/Impact
L1: Jan 28, ‘23
L2: Feb 28, ‘23
L4: Oct 28, ‘23
L3: Mar 28, ‘23
L5: Nov 28, ‘23
Challenge: Budget Availability
Implementation Team:
Project Sponsor: Musa Nabage; Onyejekwe, Chimuanya
Implementation Lead: Akinjagunla Oluwashina; Nwachukwu, Chinedu
Project SME: Idio, Samuel; Alaka, Olanrewaju
Project Team: Mukhtar Sani; Theresa Abdulmalik; Noble Uranta; Festus, Azibator
Implementation Team
Availability of requisite Funds.
Full functional support (Asset Engineering and TAs)
Availability of critical materials/procurement
Integrated Asset/Project Delivery
On time & flawless delivery
Critical Success Factors
4
5
MTO ID: I-1609386
Score: 2,500,000

## Slide 3: SOKU INSTR. AIR CAPABILITIES ANALYSIS
Capacity
Facility | Inst Air Type | 2018 | 2019 | 2020 | 2021 | 2022 | Total
Soku | AirPack Compressor (2) | $ 129,899.94 | $ 124,351.48 | $ 364,213.21 | $ 116,415.86 | $ 194,128.45 | $ 929,008.94
Gbaran | Atlas Copco Compressors (4) | $ 14,042.36 | $ 27,939.85 | $ 30,304.70 | $ 50,019.93 | $ 22,600.69 | $ 144,907.53
Parameter | Current Soku Air Pack (SFN-950) | Atlas Copco GA75+ | Atlas Copco GA55+ | Atlas Copco ZT145-10-50 (Gbaran Compressor Type) | Atlas Copco ZT160-10-50 (Proposed for SNC-2)
MWP | 10 Bar | 10 bar | 10 bar | 10 bar | 9.5 bar
Capacity | 740 Sm3/hr | 756 Sm3/hr | 562 Sm3/hr | 989.5 Sm3/hr | 1089 Sm3/hr
Installed Motor power (KW) | 132 | 74 | 60 | 160 | 160
Weight (Lbs) | 37,478 | 3,115 | 2,994 | 3,445 | 3,445
Noise Level (DB) | 85 | 68 | 66 | 67 | 69
Dryer System | Desiccant Type | Refrigerant Dryer | Refrigerant Dryer | iMD (Desiccant Type) | Desiccant Type (CD300+ASME 10 barg)
Type | Reciprocating | Oil-Injected Rotary Screw | Oil-Injected Rotary Screw | Oil-Free Rotary Screw | Oil-Free Rotary Screw
Number of Stage | 2 | 1 | 1 | 2 | 2
Cooling system | Air Cooled | Air Cooled | Air Cooled | Air Cooled | Air Cooled
Shell DEP Recommend | No | Yes | Yes | Yes | Yes

## Slide 4: Five-year cycle benefit analysis
Cost Benefit
 | Current AirPack | GA 75+ FF | GA 55+ FF | GA 45+ FF | ZT 145 | ZT 160
Unit Price (USD) |  | 67,853.44 | 60,668.31 | 51,406.83 | 177,185.25 | 178,000.00
Purchase Price x2 (USD) |  | 135,706.88 | 121,336.62 | 102,813.66 | 354,370.50 | 356,000.00
UD Filters Unit price (USD) |  | 2,134.50 | 1,808.40 | 1,604.02 |  | 0.00
UD Filters Purchase pricex2 (USD) |  | 4,269.00 | 3,616.80 | 3,208.04 | - | 0.00
2Yrs Mtce Spares | 300,000.00 | 29,855.52 | 26,694.06 | 22,619.00 | 37,584.75 | 35,000.00
2 Units + 2 Filter + 2 yrs Mtce spares | 300,000.00 | 169,831.40 | 151,647.48 | 128,640.70 | 391,955.25 | 391,000.00
Freight Cost |  | 1,826.00 | 1,826.00 | 1,826.00 | 1,826.00 | 1,826.00
VAT (7.5%) |  | 12,874.31 | 11,510.51 | 9,785.00 | 29,533.59 | 29,461.95
Site Installation Cost |  | 53,352.96 | 47,700.76 | 40,577.70 | 134,018.93 | 134,632.03
Total Upgrade Cost | $ - | $ 237,884.66 | $ 212,684.75 | $ 180,829.40 | $ 557,333.78 | $ 556,919.98
5-year Cost Saving | $ - | $1,097,706.97 | $1,203,881.11 | $1,338,230.10 | $ 165,800.66 | $ 171,410.04
10-year Cost Saving | $ - | $5,501,502.19 | $5,776,750.80 | $6,125,899.23 | $2,867,039.56 | $2,909,935.12

## Slide 5: SOKU INSTR. AIR CAPABILITIES ANALYSIS
NEXT STEPS
Raise MoC and follow-up to approval
Request new RfQ for selected compressor model and dryers
Commence coding of selected compressor model and dryers
Secure budget for procurement and installation/Obtain CC/BFM approval, as required
Initiate procurement request for compressor package and dryers, as necessary
Isolate, disconnect and remove Air Pack 1
Install & Commission Atlas Copco Pack 1
Isolate, disconnect and remove Air Pack 2
Install & Commission Atlas Copco Pack 2
Carry out Reliability Test Run
Capacity Training and Continuing to Monitor and Improve Performance