## Spares for Servicing
SEPTEMBER 2024 IA COST SAVING AS A RESULT OF OEM/ CONDITION MONITORING
S/N | IA SUSTATION | GENERATORS/CAPACITY | MATERIAL REQUIREMENT FOR SERVICING | SEPTEMBER 1ST 2024 | SEPTEMBER 30TH 2024 | RH DIFFERENCE | SERVICING BASE ON 250RH | SERVICING BASE ON CONDITION MONITORING | REMARK
1 | SUBSTATION.1 | GEN1.1690KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.8N-6309,2DRUMS RIMULAXW40 | 6975 | 7151 | 176 | NOT DUE | JULY.2024 Report/Warning
|  | GEN2.1100KVA(C32) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.287-1530&269-7041,1.5DRUMS RIMULAXW40 | 6967 | 6967 | 0 | NOT DUE | JULY.2024 Report/Warning
2 | SUBSTATION.2 | GEN1.2000KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F208-9065208-9066,2DRUMS RIMULAXW40 | 5080.9 | 5081.1 | 0.2 | NOT DUE | JULY.2024 Report/Warning
|  | GEN2.1500KVA(D3512) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.8N-3378,2DRUMS RIMULAXW40 | 4473.6 | 4636.9 | 163.3 | NOT DUE | JULY.2024 Report/Warning
3 | SUBSTATION.4 | GEN1.1000KVA(D3508) | OIL F.IR-0746,FUEL F.IR-0749,AIR 287-1530&269-7041,1.5DRUMS RIMULAXW40 | 20534 | 20660 | 126 | NOT DUE | JULY.2024 Report/Warning
|  | GEN2.500KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.8N-6309,1DRUM RIMULXW40 | 6902 | 6902 | 0 | NOT DUE | JULY.2024 Report/Warning
4 | SUBSTATION.5 | GEN1.725KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.142-1339,1DRUM RIMULXW40 | 779 | 898 | 119 | NOT DUE | JULY.2024 Report/Warning
|  | GEN2.810KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.974-1996,1DRUM RIMULXW40 | 3817 | 3817 | 0 | NOT DUE | JULY.2024 Report/Warning
5 | SUBSTATION.6 | GEN1.500KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.974-1996,1DRUM RIMULXW40 | 2956 | 3096 | 140 | NOT DUE | JULY.2024 Report/Warning
6 | SUBSTATION.7 | GEN1.1500KVA(D3512) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.8N-6309,2DRUMS RIMULAXW40 | 5208.2 | 5356.2 | 148 | NOT DUE | JULY.2024 Report/Warning
|  | GEN2.1825KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.4P-0710,2DRUMS RIMULAXW40 | 3689 | 3689 | 0 | NOT DUE | JULY.2024 Report/Warning
|  | GEN3.1100KVA(C32) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.287-1530&269-7041,1.5DRUMS RIMULAXW40 | 6947.3 | 7095.8 | 148.5 | NOT DUE | JULY.2024 Report/Warning
7 | SUBSTATION.8 | GEN1.2000KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.IF-0710,2DRUMS RIMULAXW40 | 4780 | 4898 | 118 | NOT DUE | JULY.2024 Report/Warning
|  | GEN2.1275KVA(D3512) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.4P-0710,1.5DRUMS RIMULAXW40 | 5207.6 | 5338.7 | 131.1 | NOT DUE | JULY.2024 Report/Warning
|  | GEN3.2000KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.IF-0710,1.5DRUMS RIMULAXW40 | 2485.5 | 2498.7 | 13.2 | NOT DUE | JULY.2024 Report/Warning
SEPTEMBER 2024 RA COST SAVING AS A RESULT OF OEM/ CONDITION MONITORING
S/N | SUB STATION | GEN SET | DATE LAST SERVICED | R/HRS ON SERV. DAY | CURRENT R/HRS | TOTAL RUN HOURS | FUEL FILTER | OIL FILTER | AIR FILTER | QUANTITY OF OIL
1 | SUB. 1 D3516 | GEN 2 | 2024-07-26 | 21781 | 22249 | 468 | 1R-0756 | 1R-0726 | 4P-0710 | 426 LITERS
2 | SUB. 2 D3412 | GEN 1 | 30/08/2024 | 8100 | 8348 | 248 | 1R-0749 | 1R-0716 | 142-1339 | 156 LITER
3 | SUB. 2 D3412 | GEN 2 | 30/08/2024 | 9304 | 9558 | 254 | 1R-0749 | 1R-0716 | 142-1339 | 156 LITER
4 | SUB 3 D3412 | GEN 2 | 2024-04-04 | 8289.4 | REPAIRS | REPAIRS | 1R-0749 | 1R-0716 | 142-1339
4 | SUB.3, D3512 | MOBILE | 2024-08-24 | 29120 | 29402 | 282 | 1R-0756 | 1R-0726 | 4P-0710 | 426 LITER
5 | SUB.4, D3508 | GEN. 2 | 2024-12-04 | 12929 | 13201 | 272 | 1R-0756 | 1R-0726 | 8N-6309 | 256 LITERS
6 | SUB 4 D3512 | GEN 1 | 27/07/2024 | 6098 | 6576.5 | 478.5 | 1R-0756 | 1R-0726 | 4P-0710 | 426 LITERS
6 | 2MVA MOBILE | GEN. | 2024-09-09 | 4445.6 | 4618 | 172.4 | 1R-0756 | 1R-0726 | 4P-0710 | 426 LITERS
7 | SUB 5 D3516 | GEN , 2 | 2024-09-02 | 4940 | 5323 | 346 | 1R-0756 | 1R-0726 | 4P-0710 | 420 LITERS
8 | SUB 6 D3508 | GEN. | 2024-08-25 | 8975 | 9250 | 275 | 1R-0756 | 1R-0726 | 8N-6309 | 256 LITERS
9 | SUB. 7 D3412 | GEN 1 | 2024-08-27 | 7163 | 7421 | 258 | 1R-0749 | 1R-1808 | 142-1339 | 156 LITTERS
RA SERVICING MATERIALS FOR SEPTEMBER 2024
1 | D3508 OIL FILTER | PART NO. 1R-0726 | 18 | 46000 | 828000
2 | D3508 OIL FILTER | PART NO. 1R-0756. | 30 | 23000 | 690000
3 | D3412 FUEL FILTERS | PART NO. 1R-0749. | 10 | 23000 | 230000
4 | D3412 OIL FILTERS | PART NO.1R-0716. | 10 | 46000 | 460000
5 | D3508 AIR FILTERS | PART NO. 8N-6309. | 8 | 90000 | 720000
7 | D3508 AIR FILTERS | 4P-0710 | 8 | 90000 | 720000
8 | LUBE OIL FOR SERVICING. | 16 drum | 16 | 3560.96 | 56975.36
0

## SAVING ON CONDITION MONITORING
COST SAVINGS ON SPARES AND LUBRICATION FOR THE MONTH OF SEPTEMBER 2024 IA /RA
|  | NAIRA (#) | DOLLAR ($)
| IA SAVINGS | 0 | 0
| RA SAVINGS | 3648000 | 56975.36
|  | 3648000 | 56975.36