## SPARES FOR SERVICING
AUGUST 2024 IA COST SAVING AS A RESULT OF OEM/ CONDITION MONITORING | [8 empty] | S/N | IA SUSTATION | GENERATORS/CAPACITY | MATERIAL REQUIREMENT FOR SERVICING | AUGUST 1ST 2024 | AUGUST 31ST 2024 | RH DIFFERENCE | SERVICING BASE ON 250RH | SERVICING BASE ON CONDITION MONITORING | REMARK
1 | SUBSTATION.1 | GEN1.1690KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.8N-6309,2DRUMS RIMULAXW40 | 6901 | 6973 | 72 | NOT DUE | JULY 2024 Report/Warning
|  | GEN2.1100KVA(C32) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.287-1530&269-7041,1.5DRUMS RIMULAXW40 | 5105.1 | 6967 | 1861.9 | DUE | JULY 2024 Report/Warning
2 | SUBSTATION.2 | GEN1.2000KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F208-9065208-9066,2DRUMS RIMULAXW40 | 4923.1 | 4923.1 | 0 | NOT DUE | JULY 2024 Report/Warning
|  | GEN2.1500KVA(D3512) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.8N-3378,2DRUMS RIMULAXW40 | 4281.3 | 4565.1 | 283.8 | DUE | JULY 2024 Report/Warning
3 | SUBSTATION.4 | GEN1.1000KVA(D3508) | OIL F.IR-0746,FUEL F.IR-0749,AIR 287-1530&269-7041,1.5DRUMS RIMULAXW40 | 20347 | 20525 | 178 | NOT DUE | JULY 2024 Report/Warning
|  | GEN2.500KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.8N-6309,1DRUM RIMULXW40 | 6902 | 6902 | 0 | NOT DUE | JULY 2024 Report/Warning
4 | SUBSTATION.5 | GEN1.725KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.142-1339,1DRUM RIMULXW40 | 775 | 775 | 0 | NOT DUE | JULY 2024 Report/Warning
|  | GEN2.810KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.974-1996,1DRUM RIMULXW40 | 3538 | 3817 | 279 | DUE | JULY 2024 Report/Warning
5 | SUBSTATION.6 | GEN1.500KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.974-1996,1DRUM RIMULXW40 | 2769 | 2948 | 179 | NOT DUE | JULY 2024 Report/Warning
6 | SUBSTATION.7 | GEN1.1500KVA(D3512) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.8N-6309,2DRUMS RIMULAXW40 | 5065.2 | 5199 | 133.8 | NOT DUE | JULY 2024 Report/Warning
|  | GEN2.1825KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.4P-0710,2DRUMS RIMULAXW40 | 3689 | 3689 | 0 | NOT DUE | JULY 2024 Report/Warning
|  | GEN3.1100KVA(C32) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.287-1530&269-7041,1.5DRUMS RIMULAXW40 | 6634.3 | 6933 | 298.7 | DUE | JULY 2024 Report/Warning
7 | SUBSTATION.8 | GEN1.2000KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.IF-0710,2DRUMS RIMULAXW40 | 4777 | 4777 | 0 | NOT DUE | JULY 2024 Report/Warning
|  | GEN2.1275KVA(D3512) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.4P-0710,1.5DRUMS RIMULAXW40 | 5014.7 | 5203.5 | 188.8 | NOT DUE | JULY 2024 Report/Warning
|  | GEN3.2000KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.IF-0710,1.5DRUMS RIMULAXW40 | 2296.4 | 2485.1 | 188.7 | NOT DUE | JULY 2024 Report/Warning
RA SERVICING MATERIALS FOR AUGUST 2024
1 | D3508 OIL FILTER | PART NO. 1R-0726 | 0 | 46000 | 0
2 | D3508 OIL FILTER | PART NO. 1R-0756. | 0 | 23000 | 0
3 | D3412 FUEL FILTERS | PART NO. 1R-0749. | 0 | 23000 | 0
4 | D3412 OIL FILTERS | PART NO.1R-0716. | 0 | 46000 | 0
5 | D3508 AIR FILTERS | PART NO. 8N-6309. | 0 | 90000 | 0
7 | D3508 AIR FILTERS | 4P-0710 | 0 | 90000 | 0
8 | LUBE OIL FOR SERVICING. | 11 drum | 0 | 3560.96 | 0
0

## SAVING ON CONDITION MONITORING
COST SAVINGS ON SPARES AND LUBRICATION FOR THE MONTH OF AUGUST IA
1 | SUB. 1 GEN 2 | PAT NO. | QTY | UNIT PRICE | AMOUNT (#) | AMOUNT ($)
| Oil filter | 1R-1808 | 1 | 46000 | 46000
| Fuel filter | 1R-7055 | 5 | 23000 | 115000
| Air filter | 208-9065 | 2 | 295000 | 590000
| Rimula Oil | XW40 | 1 |  |  | 3560.96
[5 empty] | 751000 | 3560.96
2 | Sub.2 Gen 2 | PAT NO. | QTY | UNIT PRICE | AMOUNT (#) | AMOUNT ($)
| Oil filter | 1R-0726 | 3 | 46000 | 138000
| Fuel filter | 1R-0749 | 5 | 23000 | 115000
| Air filter | 8N-6309 | 2 | 90000 | 180000
| Rimula Oil | XW40 | 2 |  |  | 3560.96
[5 empty] | 433000 | 7121.92
3 | Sub.5 Gen 1 | PAT NO. | QTY | UNIT PRICE | AMOUNT | AMOUNT ($)
| Oil filter | 1R-0726 | 2 | 46000 | 92000
| Fuel filter | 1R-0749 | 3 | 23000 | 69000
| Air filter | 8N-6309 | 2 | 90000 | 180000
| Rimula Oil | XW40 | 2 |  |  | 3560.96
[5 empty] | 341000 | 7121.92
4 | Sub. 7 Gen 3 | PAT NO. | QTY | UNIT PRICE | AMOUNT | AMOUNT ($)
| Oil filter | 1R-1808 | 1 | 46000 | 46000
| Fuel filter | 1R-7055 | 5 | 23000 | 115000
| Air filter | 208-9065 | 2 | 295000 | 590000
| Rimula Oil | XW40 | 1 |  |  | 3560.96
[5 empty] | 751000 | 3560.96
[5 empty] | NAIRA (#) | DOLLAR ($)
|  |  | IA SAVINGS |  | 2276000 | 21365.76
|  |  | RA SAVINGS |  | 0 | 0
[5 empty] | 2276000 | 21365.76