## Spares for Servicing
S/N | IA SUSTATION | GENERATORS/CAPACITY | MATERIAL REQUIREMENT FOR SERVICING | OCTOBER 31ST | NOVEMBER 30TH | DF | RH DIFFERENCE | SERVICING BASE ON 250RH | SERVICING BASE ON CONDITION MONITORING | REMARK
1 | SUBSTATION.1 | GEN1.1690KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.8N-6309,2DRUMS RIMULAXW40 | 6252 | 6272 | 20 | 281 | DUE | SEPTEMBER.2023 Report/Warning
|  | GEN2.1100KVA(C32) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.287-1530&269-7041,1.5DRUMS RIMULAXW40 | 3745.5 | 3745.5 | 56.3 | 56.3 | NOT DUE | SEPTEMBER.2023 Report/Warning
2 | SUBSTATION.2 | GEN1.2000KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F208-9065208-9066,2DRUMS RIMULAXW40 | 4743.2 | 4761.6 | 359.4 | 341 | DUE | SEPTEMBER.2023 Report/Warning
|  | GEN2.1500KVA(D3512) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.8N-3378,2DRUMS RIMULAXW40 | 2895 | 2928.3 | 155.3 | 122 | NOT DUE | SEPTEMBER.2023 Report/Warning
3 | SUBSTATION.4 | GEN1.1000KVA(D3508) | OIL F.IR-0746,FUEL F.IR-0749,AIR 287-1530&269-7041,1.5DRUMS RIMULAXW40 | 12596 | 12614 | 166 | 148 | NOT DUE | SEPTEMBER.2023 Report/Warning
|  | GEN2.500KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.8N-6309,1DRUM RIMULXW40 | 6902 | 6902 | 0.1 | 0.1 | NOT DUE | SEPTEMBER.2023 Report/Warning
4 | SUBSTATION.5 | GEN1.725KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.142-1339,1DRUM RIMULXW40 | 693 | 768 | 95 | 20 | NOT DUE | SEPTEMBER.2023 Report/Warning
|  | GEN2.810KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.974-1996,1DRUM RIMULXW40 | 2416 | 2417 | 153 | 152 | NOT DUE | SEPTEMBER.2023 Report/Warning
5 | SUBSTATION.6 | GEN1.500KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.974-1996,1DRUM RIMULXW40 | 5293 | 5311 | 193 | 175 | NOT DUE | SEPTEMBER.2023 Report/Warning
6 | SUBSTATION.7 | GEN1.1500KVA(D3512) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.8N-6309,2DRUMS RIMULAXW40 | 4500.6 | 4513.3 | 290.9 | 278.2 | DUE | SEPTEMBER.2023 Report/Warning
|  | GEN2.1825KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.4P-0710,2DRUMS RIMULAXW40 | 2272 | 2272 | 0.2 | 0.2 | NOT DUE | SEPTEMBER.2023 Report/Warning
|  | GEN3.1100KVA(C32) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.287-1530&269-7041,1.5DRUMS RIMULAXW40 | 5095.5 | 5113.8 | 376.9 | 358.6 | DUE | SEPTEMBER.2023 Report/Warning
7 | SUBSTATION.8 | GEN1.2000KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.IF-0710,2DRUMS RIMULAXW40 | 3964.1 | 3971 | 119.9 | 113 | NOT DUE | SEPTEMBER.2023 Report/Warning
|  | GEN2.1275KVA(D3512) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.4P-0710,1.5DRUMS RIMULAXW40 | 3692.4 | 3710.4 | 691.4 | 673.4 | DUE | SEPTEMBER.2023 Report/Warning
|  | GEN3.2000KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.IF-0710,1.5DRUMS RIMULAXW40 | 1673.7 | 1691.6 | 94.9 | 77 | NOT DUE | SEPTEMBER.2023 Report/Warning
2772.3
RA SERVICING MATERIALS FOR NOVEMBER 2023
1 | D3508 OIL FILTER | PART NO. 1R-0726 | 24 | 46000 | 1104000
2 | D3508 OIL FILTER | PART NO. 1R-0756. | 35 | 23000 | 805000
3 | D3412 FUEL FILTERS | PART NO. 1R-0749. | 16 | 23000 | 368000
4 | D3412 OIL FILTERS | PART NO.1R-0716. | 16 | 46000 | 736000
5 | D3508 AIR FILTERS | PART NO. 8N-6309. | 4 | 90000 | 360000
7 | D3508 AIR FILTERS | 4P-0710 | 11 | 90000 | 990000
8 | LUBE OIL FOR SERVICING. | 11 drum | 13 | 3560.96 | 46292.48
4363000

## SAVING ON CONDITION MONITORING
COST SAVINGS ON SPARES AND LUBRICATION FOR THE MONTH OF NOVEMBER IA /RA
1 | SUB. 1 GEN 1 | PAT NO. | QTY | UNIT PRICE | AMOUNT | AMOUNT($)
| Oil filter | 1R-0726 | 3 | 46000 | 138000
| Fuel filter | 1R-0749 | 5 | 23000 | 115000
| Air filter | 8N-6309 | 2 | 90000 | 180000
| Rimula Oil | XW40 | 2 |  |  | 3560.96
[5 empty] | 433000 | 3560.96
2 | SUB. 2 GEN 1 | PAT NO. | QTY | UNIT PRICE | AMOUNT | AMOUNT($)
| Oil filter | 1R-0726 | 3 | 46000 | 138000
| Fuel filter | 1R-0749 | 5 | 23000 | 115000
| Air filter | 8N-6309 | 2 | 90000 | 180000
| Rimula Oil | XW40 | 2 |  |  | 3560.96
[5 empty] | 433000 | 3560.96
3 | SUB. 7 GEN 1 | PAT NO. | QTY | UNIT PRICE | AMOUNT | AMOUNT($)
| Oil filter | 1R-0726 | 3 | 46000 | 138000
| Fuel filter | 1R-0749 | 5 | 23000 | 115000
| Air filter | 208-9065 | 2 | 295000 | 180000
| Rimula Oil | XW40 | 2 |  |  | 3560.96
[5 empty] | 433000 | 3560.96
0
4 | SUB. 7 GEN 3 | PAT NO. | QTY | UNIT PRICE | AMOUNT | AMOUNT($)
| Oil filter | 1R-0726 | 3 | 46000 | 138000
| Fuel filter | 1R-0749 | 5 | 23000 | 115000
| Air filter | 8N-6309 | 2 | 90000 | 180000
| Rimula Oil | XW40 | 2 |  |  | 3560.96
[5 empty] | 433000 | 3560.96
5 | Sub. 8 Gen 2 | PAT NO. | QTY | UNIT PRICE | AMOUNT | AMOUNT($)
| Oil filter | 1R-0726 | 3 | 46000 | 138000
| Fuel filter | 1R-0749 | 5 | 23000 | 115000
| Air filter | 287-1530 | 2 | 295000 | 180000
| Rimula Oil | XW40 | 2 |  |  | 3560.96
[5 empty] | 433000 | 3560.96
6 | Sub. 8 Gen 3 | PAT NO. | QTY | UNIT PRICE | AMOUNT | AMOUNT($)
| Oil filter | 1R-0726 | 3 | 46000 | 138000
| Fuel filter | 1R-0749 | 5 | 23000 | 115000
| Air filter | 8N-6309 | 2 | 90000 | 180000
| Rimula Oil | XW40 | 3 |  |  | 3560.96
[5 empty] | 433000 | 3560.96
|  |  | IA SAVINGS |  | 2598000 | 21365.76
|  |  | RA SAVINGS |  | 4363000 | 46292.48
[5 empty] | 6961000 | 67658.24