## Spares for Servicing
S/N | IA SUSTATION | GENERATORS/CAPACITY | MATERIAL REQUIREMENT FOR SERVICING | MAR.31ˢᵗ RH | APR.31ˢᵗ RH | DF | RH DIFFERENCE | SERVICING BASE ON 250RH | SERVICING BASE ON CONDITION MONITORING | REMARK
1 | SUBSTATION.1 | GEN1.1690KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.8N-6309,2DRUMS RIMULAXW40 | 5777 | 6058 | 562 | 281 | DUE | APR.2023 Report/Warning
|  | GEN2.1100KVA(C32) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.287-1530&269-7041,1.5DRUMS RIMULAXW40 | 3090.2 | 3146.5 | 112.6 | 56.3 | NOT DUE | APR.2023 Report/Warning
2 | SUBSTATION.2 | GEN1.2000KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F208-9065208-9066,2DRUMS RIMULAXW40 | 4529.6 | 4870.6 | 682 | 341 | NOT DUE | APR.2023 Report/Warning
|  | GEN2.1500KVA(D3512) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.8N-3378,2DRUMS RIMULAXW40 | 2240 | 2362 | 244 | 122 | NOT DUE | APR.2023 Report/Warning
3 | SUBSTATION.4 | GEN1.1000KVA(D3508) | OIL F.IR-0746,FUEL F.IR-0749,AIR 287-1530&269-7041,1.5DRUMS RIMULAXW40 | 1192.7 | 1340.7 | 296 | 148 | NOT DUE | APR.2023 Report/Warning
|  | GEN2.500KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.8N-6309,1DRUM RIMULXW40 | 6899.1 | 6899.2 | 0.2 | 0.1 | NOT DUE | APR.2023 Report/Warning
4 | SUBSTATION.5 | GEN1.725KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.142-1339,1DRUM RIMULXW40 | 33 | 53 | 40 | 20 | NOT DUE | APR.2023 Report/Warning
|  | GEN2.810KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.974-1996,1DRUM RIMULXW40 | 5951 | 6103 | 304 | 152 | NOT DUE | APR.2023 Report/Warning
5 | SUBSTATION.6 | GEN1.500KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.974-1996,1DRUM RIMULXW40 | 4545 | 4720 | 350 | 175 | NOT DUE | APR.2023 Report/Warning
6 | SUBSTATION.7 | GEN1.1500KVA(D3512) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.8N-6309,2DRUMS RIMULAXW40 | 3841.1 | 4119.3 | 556.4 | 278.2 | DUE | APR.2023 Report/Warning
|  | GEN2.1825KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.4P-0710,2DRUMS RIMULAXW40 | 3344.2 | 3344.4 | 0.4 | 0.2 | NOT DUE | APR.2023 Report/Warning
|  | GEN3.1100KVA(C32) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.287-1530&269-7041,1.5DRUMS RIMULAXW40 | 4240.2 | 4598.8 | 717.2 | 358.6 | DUE | APR.2023 Report/Warning
7 | SUBSTATION.8 | GEN1.2000KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.IF-0710,2DRUMS RIMULAXW40 | 3688 | 3801 | 226 | 113 | NOT DUE | APR.2023 Report/Warning
|  | GEN2.1275KVA(D3512) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.4P-0710,1.5DRUMS RIMULAXW40 | 3500 | 4173.4 | 1346.8 | 673.4 | NOT DUE | APR.2023 Report/Warning
|  | GEN3.2000KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.IF-0710,1.5DRUMS RIMULAXW40 | 1096 | 1173 | 154 | 77 | NOT DUE | APR.2023 Report/Warning
RA SERVICING MATERIALS FOR APRIL 2023
1 | D3508 OIL FILTER | PART NO. 1R-0726 | 18 | 46000 | 828000
2 | D3508 OIL FILTER | PART NO. 1R-0756. | 30 | 23000 | 690000
3 | D3412 FUEL FILTERS | PART NO. 1R-0749. | 16 | 23000 | 368000
4 | D3412 OIL FILTERS | PART NO.1R-0716. | 16 | 46000 | 736000
5 | D3508 AIR FILTERS | PART NO. 8N-6309. | 6 | 90000 | 540000
6 | D3412 AIR FILTERS | PART NO. 142-1339 | 8 | 90000 | 720000
7 | D3508 AIR FILTERS | 4P-0710 | 8 | 90000 | 720000
8 | LUBE OIL FOR SERVICING. | 11 drum | 11 | 3560.96 |  |  | 39170.56
4641170.56

## SAVING ON CONDITION MONITORING
COST SAVINGS ON SPARES AND LUBRICATION FOR THE MONTH OF APRIL IA /RA
1 | Sub. 1 Gen 1 | PAT NO. | QTY | UNIT PRICE | AMOUNT | AMOUNT($)
| Oil filter | 1R-0726 | 3 | 46000 | 138000
| Fuel filter | 1R-0749 | 5 | 23000 | 115000
| Air filter | 8N-6309 | 2 | 90000 | 180000
| Rimula Oil | XW40 | 2 |  |  | 3560.96
[5 empty] | 433000 | 3560.96
2 | Sub. 2 Gen 1
| Oil filter | 1R-0726 | 3 | 46000 | 138000
| Fuel filter | 1R-0749 | 5 | 23000 | 115000
| Air filter | 208-9065 | 2 | 295000 | 590000
| Rimula Oil | XW40 | 2 |  |  | 3560.96
[5 empty] | 843000 | 3560.96
3 | Sub. 7 Gen 1
| Oil filter | 1R-0726 | 3 | 46000 | 138000
| Fuel filter | 1R-0749 | 5 | 23000 | 115000
| Air filter | 8N-6309 | 2 | 90000 | 180000
| Rimula Oil | XW40 | 2 |  |  | 3560.96
[5 empty] | 433000 | 3560.96
4 | Sub. 7 Gen 3
| Oil filter | 1R-0726 | 3 | 46000 | 138000
| Fuel filter | 1R-0749 | 5 | 23000 | 115000
| Air filter | 287-1530 | 2 | 295000 | 590000
| Rimula Oil | XW40 | 2 |  |  | 3560.96
[5 empty] | 843000 | 3560.96
3 | Sub. 7 Gen 2
| Oil filter | 1R-0726 | 3 | 46000 | 138000
| Fuel filter | 1R-0749 | 5 | 23000 | 115000
| Air filter | 8N-6309 | 2 | 90000 | 180000
| Rimula Oil | XW40 | 2 |  |  | 3560.96
[5 empty] | 433000 | 3560.96
4 | Sub. 4 Gen 1
| Oil filter | 1R-0726 | 3 | 46000 | 138000
| Fuel filter | 1R-0749 | 5 | 23000 | 115000
| Air filter | 287-1530 | 2 | 295000 | 590000
| Rimula Oil | XW40 | 1 |  |  | 3560.96
[5 empty] | 843000 | 3560.96
3 | Sub. 8 Gen 2
| Oil filter | 1R-0726 | 3 | 46000 | 138000
| Fuel filter | 1R-0749 | 5 | 23000 | 115000
| Air filter | 8N-6309 | 2 | 90000 | 180000
| Rimula Oil | XW40 | 1 |  |  | 3560.96
[5 empty] | 433000 | 3560.96
|  |  | IA SAVINGS |  | 4261000 | 17804.8
|  |  | RA SAVINGS |  | 4641170.56 | 39170.56
[5 empty] | 8902170.56 | 56975.36