## Spares for Servicing
S/N | IA SUSTATION | GENERATORS/CAPACITY | MATERIAL REQUIREMENT FOR SERVICING | JULY 30TH | AUGUST 31ST | DF | RH DIFFERENCE | SERVICING BASE ON 250RH | SERVICING BASE ON CONDITION MONITORING | REMARK
1 | SUBSTATION.1 | GEN1.1690KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.8N-6309,2DRUMS RIMULAXW40 | 6165 | 6251 | 86 | 281 | NOT DUE | JUNE.2023 Report/Warning
|  | GEN2.1100KVA(C32) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.287-1530&269-7041,1.5DRUMS RIMULAXW40 | 3202.8 | 3457 | 310.5 | 56.3 | NOT DUE | JUNE.2023 Report/Warning
2 | SUBSTATION.2 | GEN1.2000KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F208-9065208-9066,2DRUMS RIMULAXW40 | 4656.6 | 4732.5 | 416.9 | 341 | DUE | JUNE.2023 Report/Warning
|  | GEN2.1500KVA(D3512) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.8N-3378,2DRUMS RIMULAXW40 | 2863.2 | 2892 | 150.8 | 122 | NOT DUE | JUNE.2023 Report/Warning
3 | SUBSTATION.4 | GEN1.1000KVA(D3508) | OIL F.IR-0746,FUEL F.IR-0749,AIR 287-1530&269-7041,1.5DRUMS RIMULAXW40 | 12503 | 12580 | 225 | 148 | NOT DUE | JUNE.2023 Report/Warning | Gen set is due for top overhaul.
|  | GEN2.500KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.8N-6309,1DRUM RIMULXW40 | 6899.3 | 6901 | 0.2 | 0.1 | NOT DUE | JUNE.2023 Report/Warning
4 | SUBSTATION.5 | GEN1.725KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.142-1339,1DRUM RIMULXW40 | 73 | 100 | 40 | 20 | NOT DUE | JUNE.2023 Report/Warning
|  | GEN2.810KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.974-1996,1DRUM RIMULXW40 | 2350 | 2413 | 215 | 152 | NOT DUE | JUNE.2023 Report/Warning
5 | SUBSTATION.6 | GEN1.500KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.974-1996,1DRUM RIMULXW40 | 5151 | 5226 | 250 | 175 | NOT DUE | JUNE.2023 Report/Warning
6 | SUBSTATION.7 | GEN1.1500KVA(D3512) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.8N-6309,2DRUMS RIMULAXW40 | 4435.7 | 4471.2 | 313.7 | 278.2 | DUE | JUNE.2023 Report/Warning
|  | GEN2.1825KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.4P-0710,2DRUMS RIMULAXW40 | 2207 | 2263 | 56.2 | 0.2 | NOT DUE | JUNE.2023 Report/Warning
|  | GEN3.1100KVA(C32) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.287-1530&269-7041,1.5DRUMS RIMULAXW40 | 4928 | 5066 | 496.6 | 358.6 | DUE | JUNE.2023 Report/Warning
7 | SUBSTATION.8 | GEN1.2000KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.IF-0710,2DRUMS RIMULAXW40 | 3913 | 3964.1 | 164.1 | 113 | NOT DUE | JUNE.2023 Report/Warning
|  | GEN2.1275KVA(D3512) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.4P-0710,1.5DRUMS RIMULAXW40 | 3540.3 | 3625.6 | 758.7 | 673.4 | DUE | JUNE.2023 Report/Warning
|  | GEN3.2000KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.IF-0710,1.5DRUMS RIMULAXW40 | 1520.7 | 1609.6 | 165.9 | 77 | NOT DUE | JUNE.2023 Report/Warning
RA SERVICING MATERIALS FOR AUGUST 2023
1 | D3508 OIL FILTER | PART NO. 1R-0726 | 18 | 46000 | 828000
2 | D3508 OIL FILTER | PART NO. 1R-0756. | 35 | 23000 | 805000
3 | D3412 FUEL FILTERS | PART NO. 1R-0749. | 16 | 23000 | 368000
4 | D3412 OIL FILTERS | PART NO.1R-0716. | 16 | 46000 | 736000
5 | D3508 AIR FILTERS | PART NO. 8N-6309. | 4 | 90000 | 360000
7 | D3508 AIR FILTERS | 4P-0710 | 6 | 90000 | 540000
8 | LUBE OIL FOR SERVICING. | 11 drum | 13 | 3560.96 | 46292.48 |  | 39170.56
3637000

## SAVING ON CONDITION MONITORING
COST SAVINGS ON SPARES AND LUBRICATION FOR THE MONTH OF AUGUST IA /RA
1 | SUB. 2 GEN 1 | PAT NO. | QTY | UNIT PRICE | AMOUNT | AMOUNT($)
| Oil filter | 1R-0726 | 3 | 46000 | 138000
| Fuel filter | 1R-0749 | 5 | 23000 | 115000
| Air filter | 8N-6309 | 2 | 90000 | 180000
| Rimula Oil | XW40 | 2 |  |  | 3560.96
[5 empty] | 433000 | 3560.96
2 | SUB.1 GEN 1
| Oil filter | 1R-0726 | 3 | 46000 | 138000
| Fuel filter | 1R-0749 | 5 | 23000 | 115000
| Air filter | 208-9065 | 2 | 295000 | 590000
| Rimula Oil | XW40 | 2 |  |  | 3560.96
[5 empty] | 843000 | 3560.96
3 | Sub. 7 Gen 1
| Oil filter | 1R-0726 | 3 | 46000 | 138000
| Fuel filter | 1R-0749 | 5 | 23000 | 115000
| Air filter | 8N-6309 | 2 | 90000 | 180000
| Rimula Oil | XW40 | 2 |  |  | 3560.96
[5 empty] | 433000 | 3560.96
4 | Sub. 7 Gen 3
| Oil filter | 1R-0726 | 3 | 46000 | 138000
| Fuel filter | 1R-0749 | 5 | 23000 | 115000
| Air filter | 287-1530 | 2 | 295000 | 590000
| Rimula Oil | XW40 | 2 |  |  | 3560.96
[5 empty] | 843000 | 3560.96
5 | Sub. 8 Gen 2
| Oil filter | 1R-0726 | 3 | 46000 | 138000
| Fuel filter | 1R-0749 | 5 | 23000 | 115000
| Air filter | 8N-6309 | 2 | 90000 | 180000
| Rimula Oil | XW40 | 3 |  |  | 3560.96
[5 empty] | 433000 | 3560.96
|  |  | IA SAVINGS |  | 2985000 | 17804.8
|  |  | RA SAVINGS |  | 3637000 | 46292.48
[5 empty] | 6622000 | 64097.28