## Spares for Servicing
S/N | IA SUSTATION | GENERATORS/CAPACITY | MATERIAL REQUIREMENT FOR SERVICING | JAN.1ˢᵗ RH | FEB.31ˢᵗ RH | RH DIFFERENCE | SERVICING BASE ON 250RH | SERVICING BASE ON CONDITION MONITORING | REMARK
1 | SUBSTATION.1 | GEN1.1690KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.8N-6309,2DRUMS RIMULAXW40 | 5496 | 5777 | 281 | DUE | DEC.2022 Report/Warning
|  | GEN2.1100KVA(C32) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.287-1530&269-7041,1.5DRUMS RIMULAXW40 | 3033.9 | 3090.2 | 56.3 | NOT DUE | DEC.2022 Report/Low Alert
2 | SUBSTATION.2 | GEN1.2000KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F208-9065208-9066,2DRUMS RIMULAXW40 | 4407.6 | 4529.6 | 341 | NOT DUE | DEC.2022 Report/Warning
|  | GEN2.1500KVA(D3512) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.8N-3378,2DRUMS RIMULAXW40 | 1899 | 2240 | 122 | NOT DUE | DEC.2022 Report/Low Alert
3 | SUBSTATION.4 | GEN1.1000KVA(D3508) | OIL F.IR-0746,FUEL F.IR-0749,AIR 287-1530&269-7041,1.5DRUMS RIMULAXW40 | 1177.9 | 1192.7 | 148 | NOT DUE | DEC.2022 Report/Warning
|  | GEN2.500KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.8N-6309,1DRUM RIMULXW40 | 6898 | 6899.1 | 0.1 | NOT DUE | DEC.2022 Report/Low Alert
4 | SUBSTATION.5 | GEN1.725KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.142-1339,1DRUM RIMULXW40 | 13 | 33 | 20 | NOT DUE | DEC.2022 Report/Low Alert
|  | GEN2.810KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.974-1996,1DRUM RIMULXW40 | 5799 | 5951 | 152 | NOT DUE | DEC.2022 Report/Low Alert
5 | SUBSTATION.6 | GEN1.500KVA(D3412) | OIL F.IR-0726,FUEL F.IR-0716,AIR F.974-1996,1DRUM RIMULXW40 | 4370 | 4545 | 175 | NOT DUE | DEC.2022 Report/Warning
6 | SUBSTATION.7 | GEN1.1500KVA(D3512) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.8N-6309,2DRUMS RIMULAXW40 | 3562.9 | 3841.1 | 278.2 | DUE | DEC.2022 Report/Warning
|  | GEN2.1825KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.4P-0710,2DRUMS RIMULAXW40 | 3344 | 3344.2 | 0.2 | NOT DUE | DEC.2022 Report/Low Alert
|  | GEN3.1100KVA(C32) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.287-1530&269-7041,1.5DRUMS RIMULAXW40 | 3881.6 | 4240.2 | 358.6 | DUE | DEC.2022 Report/Warning
7 | SUBSTATION.8 | GEN1.2000KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.IF-0710,2DRUMS RIMULAXW40 | 3575 | 3688 | 113 | NOT DUE | DEC.2022 Report/Low Alert
|  | GEN2.1275KVA(D3512) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.4P-0710,1.5DRUMS RIMULAXW40 | 2764.6 | 2969 | 204.4 | NOT DUE | DEC.2022 Report/Warning
|  | GEN3.2000KVA(D3516) | OIL F.IR-0746,FUEL F.IR-0749,AIR F.IF-0710,1.5DRUMS RIMULAXW40 | 1019 | 1096 | 77 | NOT DUE | DEC.2022 Report/Low Alert

## SAVING ON CONDITION MONITORING
COST SAVINGS ON SPARES AND LUBRICATION FOR THE MONTH
1 | Sub. 1 Gen 1 | PAT NO. | QTY | UNIT PRICE | AMOUNT | AMOUNT($) | REMARK
| Oil filter | 1R-0726 | 3 | 46000 | 138000 |  | The run hours of the gen set now is 281 but due to the use of condition monitoring system introduced is still ok and running.
| Fuel filter | 1R-0749 | 5 | 23000 | 115000
| Air filter | 8N-6309 | 2 | 90000 | 180000
| Rimula Oil | XW40 | 2 |  |  | 3560.96
[5 empty] | 433000 | 3560.96
2 | Sub. 2 Gen 1
| Oil filter | 1R-0726 | 3 | 46000 | 138000
| Fuel filter | 1R-0749 | 5 | 23000 | 115000 |  | The run hours of the gen set now is 341.
| Air filter | 208-9065 | 2 | 295000 | 590000
| Rimula Oil | XW40 | 2 |  |  | 3560.96
[5 empty] | 843000 | 3560.96
3 | Sub. 7 Gen 1
| Oil filter | 1R-0726 | 3 | 46000 | 138000
| Fuel filter | 1R-0749 | 5 | 23000 | 115000 |  | The run hours of the gen set now is 278.2.
| Air filter | 8N-6309 | 2 | 90000 | 180000
| Rimula Oil | XW40 | 2 |  |  | 3560.96
[5 empty] | 433000 | 3560.96
4 | Sub. 7 Gen 3
| Oil filter | 1R-0726 | 3 | 46000 | 138000
| Fuel filter | 1R-0749 | 5 | 23000 | 115000 |  | The run hours of the gen set now is 358.6
| Air filter | 287-1530 | 2 | 295000 | 590000
| Rimula Oil | XW40 | 2 |  |  | 3560.96
[5 empty] | 843000 | 3560.96
[5 empty] | 2552000 | 14243.84 | 19783.2366