## Slide 1
ELECTRIFICATION OF JTF CAMP AT UBIE FLOWSTATION
Jan 2023
Improve Power Availability , Cost Savings , Reduction in GHG,
Project Charter

## Slide 2: Project Title: Electrification of JTF Camp at Ubie Flow Station
The project seeks to supply electric power from the Ubie Flow Station Switchboard to the JTF Camp-1& Camp-2 due to surplus electrical power on both the Gas and Diesel Generators in Ubie Flow Station, that are both currently loaded at 30%. At the completion of the project, additional load from the Camp will be 37.8%. Total generators capacity loading shall then be 67.8%. This results in a spinning reserve of 24.3% if any of the generators is fully loaded during Peak period.
The project is to be executed in phases. Phase-1 will involve cable route excavation of depth 0.75m and length 120 meters. Phase-2 involves laying and termination of a 4 Core x 70mm2 XLPE Armored cable with 1C X 70mm2 Parallel Earth Conductor (PEC) over a length of 120meters. mPhase-3 involves termination of installed cables to existing 2 Isolator Circuit Breakers at both flow station and Camp-1 & Camp-2 ends, then extended to a Consumer Unit in the JTF Camp-1 & Camp-2 and lastly, testing and commissioning of the project.
The provision of power to the Camp-1 & Camp-2, after completion, will result in improved comfort of security personnel due to improved power availability and reliability for effective security coverage to personnel and asset and huge reduction in both GHG emission and OpEx on AGO.
It will reduce Greenhouse gas Emission from Diesel Engines
Improve power supply availability and reliability at JTF Camp-1 & Camp-2.
Cost savings. (Opex)
Potential Benefits & Measurement:
Business Case/Objectives:
Availability of station up time step to 99.5%
Cables should be buried under ground and slab , for addition safety and security measures.
Surveillance on oil export line using the LDS (Leak detection system) to reduce down time of flow station.
Critical Success Factors:
Management of Change Request, Development and approval.
Procurement and supply of power cables.
Execution at site and Commissioning .
Secure necessary funding.
Project Scope:
Challenge :Budget Availability
Implementation Lead: Okolo Nelson
Project Sponsor: Bayo Balogun
Implementation:
CV
CV
CV
CV
1
2
3
4
5