## DCS Upgrade Issues (hidden)
S/N | Issues | Description | Action to be Taken by Party | Criticality A-Must do Now, B- Can Do Now, C- Can do Later | Status
1 | MOS switch mapping to the DCS tags | Enabling an MOS for a specific SIS tag may be found active on another SIS tag | Testing on individual MOS switches to be done for each tag | A | CLOSED
2 | Correct OOS switch mapping to units on DCS | Enabling an OOS for a specific unit should activate all group tags | Testing of individual OOS switches to be done and confirm every corresponding tag receives it on the DCS | A | CLOSED
3 | ESD Tree is active on all units graphics in the DCS | ESD Tree should be active only when the is a trip. Plant cannot be live while ESD Tree is active | Yokogwa to correct | A | CLOSED
4 | Incomplete CAMS and Incomplete Historical Report Operation and Montitoring Log on Engineering Work Station | Trip on 66LZA-515 did not show upo on CAMS and also did not show up on Historical log. unable to see all events with sequence message checked and launched via Historical report (SLS) | Yokogawa will review with back office and provide solution 23.11.2023 Yokogawa to ensure Process Alarms in CAMs for all domain is complete.(High Priority Alarms, Medium Priority Alarms and Low Prioriity Alarms | A | OPEN
5 | CAMS shows domain2 alarm on (IOP Still) | IOP Still Critical Alarm displays on Alarm CAMS HIS Message Monitor (Only 63Q1 on IOP Still) | Yokogwa to correct | B | CLOSED
6 | CAMs is incomplete in HIS. (E.g High Priority Process Alarms is Zero, fewer than expected Medium Priority Alarms. | Historical Report Operation and Montitoring Log not complete for all categories of alarms Operators with same S2 security level do not see the same enteries in CAMS. | Yokogwa to correct | A | OPEN
7 | DCS tags values on graphics and RAW values are inconsistent | 45PIA-311 is "XXXXX" RAW value 10PCV-800 not responding as controller is on IMAN 45PZA301A is 13.4 barg on DCS but 78 barg in the field 68PI-004 reads 8.9barg in DCS but 55.7 RAW value 55PZA-413 reading disparity between field and DCS |  | A | CLOSED
8 | Control valves working normally before the upgrade are found reverse action. | 52LICA-001 opens when command is CLOSE and closes when command is OPEN | Yokogawa to check. The PID Control _Action parameter went to Reverse post upgrade. This was corrected to DIRECT. Control loop working but the % opening is showing 100% instead of 0% | A | CLOSED
9 | Control valves working normally before the upgrade are found reverse action. | 52PCV-001 opens when command is CLOSE and closes when command is OPEN | Yokogawa to check. The PID Control _Action parameter went to Reverse post upgrade. This was corrected to DIRECT. Control loop working but the % opening is showing 100% instead of 0% | A | CLOSED
10 | 45 PCV 014 on EGGS metering line does not take operator's input on MAN mode | valve cannot be opened from its faceplate on manual mode. |  | A | Closed
11 | Pump 5501A/B/C not starting on REMOTE. | Pump C is ON on DCS while it is OFF in the field | PACO/Yokogawa to carryout checks and resolve issues | B | Closed
12 | GSGW-0144 OPC Server hand shake with sub-systems (LPNAG, AG2, Metering) not established | Tags from Metering, AG2, LPNAG are not streaming on DCS | Yokogawa and PCD-IT(Soku) |  | OPEN
13 | GSGW0138 OPC Server handshake between Gbaran DeltaV and Soku DCS not complete. | KS2 NAG Flowline Production Header tags in Gbaran are not available on Soku DCS | Yokogawa and PCD-IT (Gbaran and Soku) | B | OPEN
14 | Solar unit GT2 and GTS 3 tags not streaming on DCS | Yokogawa to re-engineering work with Solar so that the tags on GT2 nad GT3 will stream on DCS | Solar and Yokogawa to liaise and correct Yokogawa to send a proposal | B | OPEN
15 | Wrong Power Generators status on DCS | Solar Generators Status for GT121 incorrect | Solar and Yokogawa to liaise and correct | B | OPEN
16 | 32UZ-007 working in reverse, | Valve needs to work according to command | PACO to check field for 24Vdc and confirm with Yokogawa if the problem is not in the field | B | CLOSED
17 | 21FIT-801 LP NAG discharge reading too low | LPNAG is up but the discharge f low is reading 134MMSCF/D while operators expected above 170MMSCF | PACO to go check the mA output and verify with DCS. If DCS value is in disparity, revert to Yokogawa | A | CLOSED
18 | 30PCV-001B on Test Separator not responding to the command from DCS | Valve was responding before TAM. But now fully open and non responsive | PACO checked and narrowed problem down to DCS -YOKOGAWA to rectify issue | A | CLOSED
19 | 10PCV-800B controlling on Manual but not on CAS as the 10PICA800C is on IMAN | Spill over valve 10PCV800 ought to operate on cascade to control the pressure of V1080 | Yokogawa to remove the IMAN on the 10PICA-800 and establish the control of 10PCV800 on CAS. | A | CLOSED
20 | 30PCV-001C Test Separator is not responding to the command from DCS | Valves was responding before TAM. But now fully open and non responsive | PACO checked and narrowed problem down to DCS -YOKOGAWA to rectify issue | A | CLOSED
21 | 55CPR04 and 55CPR-05 Graphics page not showing on HIS 0161 | When called, the page is blank | Yokogawa to corect | A | CLOSED
22 | 10LICA-800 not trending on DCS | Trend ought to show for every tag on DCS as was before upgrade | Yokogawa to corect | B | CLOSED
23 | 30LCV-001A (Test Separator) is not responding to command from DCS | Valves was responding before TAM. But now fully open and non responsive | PACO checked and narrowed problem down to DCS -YOKOGAWA to rectify issue | A | CLOSED
24 | 30PCV-001A (Test Separator) is not responding to command from DCS | 30PCV-001A (Test Separator) is not responding to command from DCS | PACO checked and narrowed problem down to DCS -YOKOGAWA to rectify issue | A | CLOSED
25 | 30LCV-001B (Test Separator) is not responding to command from DCS | Valves was responding before TAM. But now fully open and non responsive | PACO checked and narrowed problem down to DCS -YOKOGAWA to rectify issue | A | CLOSED
26 | 30PICA-001 frozen at 15 Barg while 0.0barg in the field | 15barg showing on DCS while 0 barg in the field | Yokogawa to corect | A | CLOSED
27 | 30LICA-001 not trending on DCS | Trend ought to show for every tag on DCS as was before upgrade | Yokogawa to corect | A | CLOSED
28 | P-6603A/B (ATM) Not picking on Auto as it were | Flare knockout drum pumps run only on Manual now | Yokogawa to corect | A | CLOSED
29 | 11 LIZA005HH and 11 LIZA006LL on Magenta | False Active alarmS on 11 LIZA005HH and 11 LIZA006LL | Yokogawa to corect | A | CLOSED
30 | 68PICA-005 reading 6.25 barg in the field similar to bourdon tube gauge reading 2.5bagr but on DCS this tag reads 9.69barg | DCS should read same value as the field instrumewnt at all times | Yokogawa to correct | A | CLOSED
31 | Component Check Liist | Checking if components in BOM are installed | Yokogawa to correct | A | OPEN
32 |  | Checking if communciation is established between SLS and DCS | Yokogawa to correct | A | OPEN
33 |  | Checking the quantity of spares in BOM | Yokogawa to correct | A | OPEN
34 | MULCOM Replacement SAT | De commission the old MULCOM and installing the new C0-920 | Yokogawa to correct | A | OPEN
35 |  | SOE fucntionality | Yokogawa to correct | A | OPEN
36 |  | CO-920 communication with DCS | Yokogawa to correct | A | OPEN
37 | Alarm Download Challenge | Alarm download on DCS has been seamless before TAM but now alarms take a longer time to drop | Yokogawa to correct troubleshoot and resolve | A | OPEN
38 | P-6601A/B (HP) FLKO Not picking on Auto as it were | HP Flare knockout drum pumps run only on Manual now | Yokogawa to corect | A | CLOSED
39 | Frozen values on 22G1203/22G1205/22G1214 (AG2 ASV-1st,2nd,3rd Stage-17/26/20) | Frozen values on AGC2 Anti SurgeValves values 1st, 2nd & 3rd Stages | Subsystem -YOKOGAWA /PCD-IT | B | OPEN
40 | No Trend window on 67LICA-002 | 67LICA-002 Not trending | Yokogwa to enable trend function | B | CLOSED
41 | Control valves working normally before the upgrade are found reverse action | 52LCV-001 opens when command is CLOSE and closes when command is OPEN | Yokogawa to correct | A | CLOSED
42 | OSD3 Tree is active on unit graphics | OSD3 should be active only in the event of unit trip | PACO to check conditions | A | OPEN
43 | Mulcum Replacement: CO-920-01 not communicating to the M0986 network, position 0108 | The cards have been confirmed faulty. This means no redundancy of ESD connection to PAS 311 | Yokogawa to Replace | A | OPEN
44 | CO-920-01 not communciating with the prosafe com set. Position 0116 | The cards have been confirmed faulty. This means no redundancy of F&G connection to PAS 311 | Yokogawa to Replace | A | OPEN
45 | OSD2 Tree is active on unit graphics | For example, Graphics 31CSL00, OSD2 cannot be active on Unit 41 (GRU1) while the unit itself is still running. Graphics 21CSL-01 also has OSD-2 whereas NAG Compressor is still up and running This shows it is not a field instrument related cause. | Yokogawa to Resolve | A | OPEN
46 | Cyan color now on ESD/OSDTree graphics | For example graphics 51CSL-01, 52CSL-01 It- is part of the pre-TAM color code which has either been Green or Red. | Yokogawa to Resolve | A | OPEN
47 | Flow Station upgrade has not been tested loop by loop, tag by tag | Hardware changes done(Controller) HIS.ENG stations software upgrade done but the system has not been checked to ensure issues with Soku gas plant are repeated there | Yokogawa/Soku Asset Team | C | OPEN
48 | ACE Project MOS Panel tagging not engraved for 55PZA033 | The tag for the MOS Key position for the new SIS tag 55PIZA033 is written on a masking tape but has to be engraved to avoid confusion | Yokogawa to close | C | OPEN
49 | ACE Project Cause/Effect Testing outstanding | There has not been a window to test the effects and Cause table for the ACE project | Yokogawa/Soku Asset Team | A | OPEN
50 | PCD Node STN0158, STN 0263, HIS0264, windows activation not done and patches not installed | Yokogawa has activated key codes but PCD-IT confirms by a generic code that thee windows is not activated, thus patches cannot be run on these. | Yokogawa. | A | OPEN

## OPEN ACTIONS PUNCH LIST DCS UPG
Soku Gas Plant and Flow Station DCS Upgrade Project. October 22nd -Nov 24th Punch List Items
S/N | Issues | Description | Action to be Taken by Party | Criticality A-Must do Now B- Can Do Now C- Can do Later | Status
1 | Incomplete CAMS and Incomplete Historical Report Operation and Monitoring Log on Engineering Work Station | Trip on 66LZA-515 did not show upon on CAMS and also did not show up on Historical log. unable to see all events with sequence message checked and launched via Historical report (SLS) | Yokogawa will review with back office and provide solution 23.11.2023 Yokogawa to ensure Process Alarms in CAMs for all domain is complete.(High Priority Alarms, Medium Priority Alarms and Low Priority Alarms | A | OPEN
2 | CAMs is incomplete in HIS. (E.g. High Priority Process Alarms is Zero, fewer than expected Medium Priority Alarms. | Historical Report Operation and Monitoring Log not complete for all categories of alarms Operators with same S2 security level do not see the same entries in CAMS. | Yokogwa to correct | A | OPEN
3 | GSGW-0144 OPC Server hand shake with sub-systems (LPNAG, AG2, Metering) not established | Tags from Metering, AG2, LPNAG are not streaming on DCS | Yokogawa and PCD-IT(Soku) |  | OPEN
4 | GSGW0138 OPC Server handshake between Gbaran DeltaV and Soku DCS not complete. | KS2 NAG Flowline Production Header tags in Gbaran are not available on Soku DCS | Yokogawa and PCD-IT (Gbaran and Soku) | B | OPEN
5 | Solar unit GT2 and GTS 3 tags not streaming on DCS | Yokogawa to re-engineering work with Solar so that the tags on GT2 and GT3 will stream on DCS | Solar and Yokogawa to liaise and correct Yokogawa to send a proposal | B | OPEN
6 | Wrong Power Generators status on DCS | Solar Generators Status for GT121 incorrect | Solar and Yokogawa to liaise and correct | B | OPEN
7 | Component Check List | Checking if components in BOM are installed | Yokogawa to correct | A | OPEN
8 |  | Checking if communication is established between SLS and DCS | Yokogawa to correct | A | OPEN
9 |  | Checking the quantity of spares in BOM | Yokogawa to correct | A | OPEN
10 | MULCOM Replacement SAT | De commission the old MULCOM and installing the new C0-920 | Yokogawa to correct | A | OPEN
11 |  | SOE functionality | Yokogawa to correct | A | OPEN
12 |  | CO-920 communication with DCS | Yokogawa to correct | A | OPEN
13 | Alarm Download Challenge | Alarm download on DCS has been seamless before TAM but now alarms take a longer time to drop | Yokogawa to correct troubleshoot and resolve | A | CLOSED
14 | Frozen values on 22G1203/22G1205/22G1214 (AG2 ASV-1st,2nd,3rd Stage-17/26/20) | Frozen values on AGC2 Anti Surge Valves values 1st, 2nd & 3rd Stages | Subsystem -YOKOGAWA /PCD-IT | B | CLOSED
15 | OSD3 Tree is active on unit graphics | OSD3 should be active only in the event of unit trip | PACO to check conditions | A | OPEN
16 | Mulcum Replacement: CO-920-01 not communicating to the M0986 network, position 0108 | The cards have been confirmed faulty. This means no redundancy of ESD connection to PAS 311 | Yokogawa to Replace | A | OPEN
17 | CO-920-01 not communicating with the prosafe com set. Position 0116 | The cards have been confirmed faulty. This means no redundancy of F&G connection to PAS 311 | Yokogawa to Replace | A | OPEN
18 | OSD2 Tree is active on unit graphics | For example, Graphics 31CSL00, OSD2 cannot be active on Unit 41 (GRU1) while the unit itself is still running. Graphics 21CSL-01 also has OSD-2 whereas NAG Compressor is still up and running This shows it is not a field instrument related cause. | Yokogawa to Resolve | A | OPEN
19 | Cyan colour now on ESD/OSDTree graphics | For example graphics 51CSL-01, 52CSL-01 It- is part of the pre-TAM colour code which has either been Green or Red. | Yokogawa to Resolve | A | OPEN
20 | Flow Station upgrade has not been tested loop by loop, tag by tag | Hardware changes done(Controller) HIS.ENG stations software upgrade done but the system has not been checked to ensure issues with Soku gas plant are repeated there | Yokogawa/Soku Asset Team | C | OPEN
21 | ACE Project MOS Panel tagging not engraved for 55PZA033 | The tag for the MOS Key position for the new SIS tag 55PIZA033 is written on a masking tape but has to be engraved to avoid confusion | Yokogawa to close | C | OPEN
22 | ACE Project Cause/Effect Testing outstanding | There has not been a window to test the effects and Cause table for the ACE project | Yokogawa/Soku Asset Team | A | OPEN
23 | PCD Node STN0158, STN 0263, HIS0264, windows activation not done and patches not installed | Yokogawa has activated key codes but PCD-IT confirms by a generic code that these O.S are not activated, thus patches cannot be run on these. | Yokogawa. | A | OPEN
| Yokogawa Middle East Service Enginneer |  | SPDC Asset
| Name: |  | Name: Arthur Dan-Nwaogu
| Designation |  | Designation: SPDC Soku PACO Supervisor
| Sign. |  | Sign.
| Date |  | Date 24 11 2023
| Yokogawa Middle East Manager |  | SPDC Project Execution Manager
| Name: |  | Name:
| Designation |  | Designation
| Sign. |  | Sign.
| Date |  | Date