## Slide 1: Bonny critical equipment Improvement Strategy
July 2021
Team
Bonny oil and Gas

## Slide 2: BOGT Gas Turbine Generators GTG-50/60/70
 | PROJECT | AFFECTED UNIT | CURRENT STATUS | WEEK’S UPDATE | COMMITMENT FOR NEXT WEEK | ACTION PATY | LEC
1 | Combustion Inspection | GT-50 | Vendor registration | Inspections completed, close out of findings in progress | Raise work order and mobilize Baker Hughes Mech FSR | Kene | 31/08/2021
2 | 64K Inspection | GT-60 | Vendor registration | Awaiting responses from Mitstibushi Hitachi on Business and DPR | Get up update from Hitachi on Business and DPR permit | Kene | Q4 2022
3 | Rotor trim balancing | GT-70 | Vendor registration | Awaiting responses from Mitstibushi Hitachi on Business and DPR | Get up update from Hitachi on Business and DPR permit | Kene | 31/08/2021
4 | MIG relay configuration | GT-70 | Completed |  |  |  | 
5 | Turbine Control Panel upgrade | GT-50 | Contracting | Held Meeting with NAPIMS and got support to Transmit Letter for approval | Transmit letter to NAPIMS for approval and finalize contract negotiation | Kene | 30/11/2021
6 | Generator Protection Panel upgrade | GT-50 | Contracting | Held meeting with NAPIMS and got support to transmit Letter for approval | Finalize the budgetary quote and transmit letter to NAPIMS for approval | Kene | 01/12/2021
7 | Procurement of UPS/critical spares | GT-50/60/70 | Awaiting NAPIMS approval | Held meeting with NAPIMS and got support to transmit Letter for approval | Finalize the budgetary quote and transmit letter to NAPIMS for approval | Kene | 31/12/2021

## Slide 3: BOGT Gas Turbine Generator Solar 10
Week's update |  | 
 | Activity | status
1 | Rectify faulty Battery room Vent fan | Completed
2 | Replace Indicator lamps on the MCC | Completed
3 | Change out Engine and Enclosure Air Inlet Filter elements | Coding ongoing
4 | Change out Main Lube Oil Filter elements | 2pcs found in FOT warehouse. Following up for transfer to BOGT
Look ahead | 
1 | Transfer of lube oil filters to Bonny
2 | Change out Gas Fuel filter elements
3 | Change out the corroded Ignitor plug
4 | Order replacement for defective gauges
Challenge
Turbine performance and reliability impacted by fuel gas quality
Fuel gas supply to the Solar Turbines is from BNAG with no adequate treatment to meet the required specification
Update
EWR raised to change source of fuel gas to OGGS plant
Support required
Execute change of Solar Turbine fuel gas supply source – Chisom

## Slide 4: AGS and Gas Gens
AGS
  Engine overhaul completed
  Unit currently running
Gas Gen B
  Top engine overhaul completed, awaiting final finetuning
  Finetuning on hold due to faulty battery
  PR 10723650 approved for battery procurement; awaiting PO
  Look Ahead:
  Issue PO for battery procurement – Okey Nweze
  Support required
  Expedite PR 0723650
Gas Gen A
  In operation
  Awaiting Gen B readiness to commence engine overhaul

## Slide 6: SS100 Smouldering
Progress Update – SS100 Smouldering:
Problem: Smouldering incident in BOGT sub station 100 switch board panels.
Suspected Cause:
  Poor protection system
  Cable over heating
Potential Causative Factors:
  Possible over run high voltage equipment leading to a higher-than-normal cable temperature.
  Unavailability of earthing protection cables due to theft
Update:
  Provide inventory of the damaged spares
  Carried out isolation of the panel
  Deep dive/Technical review of proposal done by TA
  Place standing instruction of the use of the fire water pumps
  Rectified the functionality of the electric jockey pumps
  Received scope quotation by CP after OEM (Eaton Holec) engagement
  OEM rep site visit done.
  Updated quotation received and with C&P buyer.
Look Ahead:
  Receive quotes from “potential OEM reps” to progress activity.
Outstanding Issues/Spares:
Engage alternate buyers to benchmark spare procurement cost – Benaiah 23rd June 2021
Support Required:
Support needed to nudge the C&P buyer to complete engagement with other “potential OEM reps” to progress activity- Akinola/Benaiah 15th July 2021
Line approval for execution contract using Teco (OEM Vendor)
- Budget 500k Euros – TBA