## ESD
|  |  |  | 2018 | 2019 | 2020
|  |  | CM Costs | 8147.2 | 31858.11 | 7638
|  |  | CM count | 13 | 38 | 52
Failure Modes
Assets | Failure Mode | Frequency
Hardware | Valve - External leakage | 3
| Valve - Passing | 1
| Valve - Stuck or fails on demand | 26
| Valve - Slow response time | 3
| Actuator failure | 2
Miscellaneous | Discrepancy alarm fault | 44
| Air filter regulator failure | 10
| Mod_Bad Alarm fault | 6
| Positioner failure | 5
| Hardware- related failures | 35
| Miscellaneous - related failures | 65

## Bad Actors
Bad Actor Transmitters
S/N | Tag No. | Freq. of faults | Remarks
1 | 52SDV340 | 5 | All Disc_Alarms faults
2 | 52SDV241 | 4 | Disc_Alarm faults (3ce)
3 | 51SDV242 | 4 | EPAF ESD valve closure time (3ce)
4 | 51SDV121 | 3 | Disc_Alarm faults (1ce), other failures
5 | 52SDV240 | 3 | Disc_Alarms faults (3ce)
6 | 53SDV120 | 3 | Disc_Alarms faults (3ce)
7 | 53SDV220 | 3 | Disc_Alarms faults (2ce)

## Notifications
Required End | Priority | Notification | Breakdown | Description | Functional Location | Notification date | System status | User Status | Created On | Equipment | Maintenance Plan | Order | Priority type | Priority text | SCE Group | ABC indicator | Catalog profile | FunctLocDescrip. | Object Description | Completion by date | Master insp.charac. | Notification type
20210209 | 7 | 11772245 | X | 09SDV112 Solenoid valve DIS_ALM Fault | NG.AFA.OKOG1.ES.09SDV112 | 2020-02-15 | NOCO ORAS | CLSD | 2020-02-15 | 31000136585 |  | 22822793 | CM | Complete by 12 Mths | SD006 | A | CP_INS204 | SD VLV, ESD SYS(A-09-01 MANIFOLD),OKOG1 | ROTORK GP-085S-535A/C7/FB SD VLV | 2020-03-04 |  | Z1
20200809 | 6 | 11771339 |  | 10SDV901 Solenoid Valve DIS_ALM Fault | NG.AFA.OKOG1.ES.10SDV901 | 2020-02-11 | NOCO ORAS | CLSD | 2020-02-11 | 31000136596 |  | 22821885 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(WELL F10F14-22),OKOG1 | ROTORK CP/S-045-120A/A/RB SD VLV | 2020-03-07 |  | Z1
20200809 | 6 | 11771339 |  | 10SDV901 Solenoid Valve DIS_ALM Fault | NG.AFA.OKOG1.ES.10SDV901 | 2020-02-11 | NOCO ORAS | CLSD | 2020-02-11 | 31000136596 |  | 22821885 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(WELL F10F14-22),OKOG1 | ROTORK CP/S-045-120A/A/RB SD VLV | 2020-03-07 |  | Z1
20200808 | 6 | 11771125 |  | 46SDV915 Solenoid Valve DIS_ALM Fault | NG.AFA.OKOG1.ES.46SDV915 | 2020-02-10 | NOCO ORAS | CLSD | 2020-02-10 | 31000136706 |  | 22821629 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(NGC METERING),OKOG1 | ROTORK CP/S-045-120A/A/RB SD VLV | 2020-03-08 |  | Z1
20200905 | 6 | 11776674 |  | 51SDV121/DIS_ALM Fault | NG.AFA.OKOG1.ES.51SDV121 | 2020-03-09 | NOCO ORAS | CLSD | 2020-03-09 | 31000136747 |  | 22828443 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(XHP DRUM 1),OKOG1 | ROTORKCP/S065-280A/B+A90R/259MGV900SDV | 2020-04-06 |  | Z1
20200808 | 6 | 11771133 |  | 51SDV210 Solenoid Valve DIS_ALM Fault | NG.AFA.OKOG1.ES.51SDV210 | 2020-02-10 | NOCO ORAS | CLSD | 2020-02-10 | 31000136749 |  | 22821632 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(H.P. DRUM 1),OKOG1 | ROTORKCP/S045-180A/C+A90R/259MGV900SDV | 2020-03-06 |  | Z1
20200904 | 6 | 11776541 |  | 51SDV240/DIS_ALM Fault | NG.AFA.OKOG1.ES.51SDV240 | 2020-03-08 | NOCO ORAS | CLSD | 2020-03-08 | 31000136751 |  | 22828433 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(COND HEATER 1),OKOG1 | ROTORK CP/S-045-140/A SD VLV | 2020-04-06 |  | Z1
20200904 | 6 | 11776566 |  | 51SDV241/DIS_ALM Fault | NG.AFA.OKOG1.ES.51SDV241 | 2020-03-08 | NOCO ORAS | CLSD | 2020-03-08 | 31000136752 |  | 22828440 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(H.P. DRUM 1),OKOG1 | ROTORKCP/S065-280A/B+A90R/259MGV900SDV | 2020-04-01 |  | Z1
20200904 | 6 | 11776542 |  | 51SDV242/DIS_ALM Fault | NG.AFA.OKOG1.ES.51SDV242 | 2020-03-08 | NOCO ORAS | CLSD | 2020-03-08 | 31000136753 |  | 22828438 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(COND HEATER 1),OKOG1 | ROTORK CP/S-045-140/B SD VLV | 2020-04-02 |  | Z1
20200904 | 6 | 11776603 |  | 51SDV340 Solenoid Valve DIS_ALM Fault | NG.AFA.OKOG1.ES.51SDV340 | 2020-03-08 | NOCO ORAS | CLSD | 2020-03-08 | 31000136757 |  | 22828442 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(L.P. DRUM 1),OKOG1 | ROTORK CP/S-035-100A/B SD VLV | 2020-04-07 |  | Z1
20200904 | 6 | 11776538 |  | 52SDV121/DIS_ALM Fault | NG.AFA.OKOG1.ES.52SDV121 | 2020-03-08 | NOCO ORAS | CLSD | 2020-03-08 | 31000136790 |  | 22828436 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(XHP DRUM 2),OKOG1 | ROTORKCP/S-045-180/C-A90R/259MGV900SDV | 2020-04-05 |  | Z1
20200719 | 6 | 11767178 | X | 52SDV220 Discrepancy Alarm fault | NG.AFA.OKOG1.ES.53GIT220 | 2020-01-21 | NOCO ORAS | CLSD | 2020-01-21 |  |  | 22813842 | CM | Complete by 6 Months |  | C | CP_INS202 | GIT, 53SDV220 SD VLV, ESD SYS, OKOG1 |  | 2020-02-01 |  | Z1
20190210 | 4 | 11692669 |  | 52SDV240/DIS_ALM at H.P. DRUM 2 | NG.AFA.OKOG1.ES.52SDV240 | 2019-01-13 | NOCO ORAS | CLSD | 2019-01-13 | 31000136794 |  | 22736791 | CM | Complete by 4 Weeks | SD006 | A | CP_INS204 | SD VLV, ESD SYS(H.P. DRUM 2),OKOG1 | ROTORK CP/S-045-140A/B SD VLV | 2019-01-23 |  | Z1
20200904 | 6 | 11776540 |  | 52SDV240/DIS_ALM Fault | NG.AFA.OKOG1.ES.52SDV240 | 2020-03-08 | NOCO ORAS | CLSD | 2020-03-08 | 31000136794 |  | 22828437 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(H.P. DRUM 2),OKOG1 | ROTORK CP/S-045-140A/B SD VLV | 2020-04-04 |  | Z1
20200719 | 6 | 11767177 | X | 52SDV241 Discrepancy Alarm fault | NG.AFA.OKOG1.ES.52SDV241 | 2020-01-21 | NOCO ORAS | CLSD | 2020-01-21 | 31000136795 |  | 22813874 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(H.P. DRUM 2),OKOG1 | ROTORKCP/S065-280A/B+A90R/259MGV900SDV | 2020-01-31 |  | Z1
20190210 | 4 | 11692670 |  | 52SDV241/DIS_ALM at H.P. DRUM 2 | NG.AFA.OKOG1.ES.52SDV241 | 2019-01-13 | NOCO ORAS | CLSD | 2019-01-13 | 31000136795 |  | 22736792 | CM | Complete by 4 Weeks | SD006 | A | CP_INS204 | SD VLV, ESD SYS(H.P. DRUM 2),OKOG1 | ROTORKCP/S065-280A/B+A90R/259MGV900SDV | 2019-01-23 |  | Z1
20200903 | 6 | 11776442 | X | 52SDV241/DIS_ALM Fault | NG.AFA.OKOG1.ES.52SDV241 | 2020-03-07 | NOCO ORAS | CLSD | 2020-03-07 | 31000136795 |  | 22828222 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(H.P. DRUM 2),OKOG1 | ROTORKCP/S065-280A/B+A90R/259MGV900SDV | 2020-03-23 |  | Z1
20200904 | 6 | 11776553 |  | 52SDV242/DIS_ALM Fault | NG.AFA.OKOG1.ES.52SDV242 | 2020-03-08 | NOCO ORAS | CLSD | 2020-03-08 | 31000136796 |  | 22828439 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(H.P. DRUM 2),OKOG1 | ROTORK CP/S-045-140A/B SD VLV | 2020-04-02 |  | Z1
20201212 | 5 | 11815203 |  | 52SDV340 Solenoid Valve DIS_ALM Fault | NG.AFA.OKOG1.ES.52SDV340 | 2020-10-17 | NOCO ORAS | CLSD | 2020-10-17 | 31000136800 |  | 22875887 | CM | Complete by 8 Weeks | SD006 | A | CP_INS204 | SD VLV, ESD SYS(L.P. DRUM 2),OKOG1 | ROTORK CP/S-055-200A/A SD VLV | 2020-11-15 |  | Z1
20200904 | 6 | 11776598 |  | 52SDV340 Solenoid Valve DIS_ALM Fault | NG.AFA.OKOG1.ES.52SDV340 | 2020-03-08 | NOCO ORAS | CLSD | 2020-03-08 | 31000136800 |  | 22828441 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(L.P. DRUM 2),OKOG1 | ROTORK CP/S-055-200A/A SD VLV | 2020-04-01 |  | Z1
20210209 | 7 | 11772244 |  | 52SDV340 Solenoid Valve DIS_ALM Fault | NG.AFA.OKOG1.ES.52SDV340 | 2020-02-15 | NOCO ORAS | CLSD | 2020-02-15 | 31000136800 |  | 22822792 | CM | Complete by 12 Mths | SD006 | A | CP_INS204 | SD VLV, ESD SYS(L.P. DRUM 2),OKOG1 | ROTORK CP/S-055-200A/A SD VLV | 2020-03-03 |  | Z1
20201230 | 4 | 11823946 |  | 53SDV110 INCESSANT FAILURE/DIS_ALM | NG.AFA.OKOG1.ES.53SDV110 | 2020-12-02 | NOCO ORAS | CLSD | 2020-12-02 | 31000136817 |  | 22884395 | CM | Complete by 4 Weeks | SD006 | A | CP_INS204 | SD VLV, ESD SYS(COND TANK A),OKOG1 | ROTORK CP/S-035-100A/B SD VLV | 2020-12-24 |  | Z1
20210204 | 6 | 11802294 |  | 53SDV120/DIS_ALM Fault | NG.AFA.OKOG1.ES.53SDV120 | 2020-08-08 | NOCO ORAS | CLSD | 2020-08-08 | 31000136818 |  | 22863524 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(COND TANK A),OKOG1 | ROTORK CP/S-035-100A/B SD VLV | 2020-09-29 |  | Z1
20210209 | 7 | 11772240 |  | 53SDV220 Solenoid Valve DIS_ALM fault | NG.AFA.OKOG1.ES.53SDV220 | 2020-02-15 | NOCO ORAS | CLSD | 2020-02-15 | 31000136821 |  | 22822791 | CM | Complete by 12 Mths | SD006 | A | CP_INS204 | SD VLV, ESD SYS(COND TANK B),OKOG1 | ROTORK CP/S-035-100A/B SD VLV | 2020-03-07 |  | Z1
20200809 | 6 | 11771347 |  | 53SDV301 Solenoid Valve DIS_ALM Fault | NG.AFA.OKOG1.ES.53SDV301 | 2020-02-11 | NOCO ORAS | CLSD | 2020-02-11 | 31000190981 |  | 22821886 | CM | Complete by 6 Months | SD001 | A | CP_INS204 | SHUTDWN VLV301, CONDENSATE PPKG-5302, ES | TK MODEL BS6RA74333 SHUTDOWN VALVE | 2020-03-03 |  | Z1
20210209 | 7 | 11772247 |  | 53SDV305 Solenoid Valve DIS_ALM Fault | NG.AFA.OKOG1.ES.53SDV305 | 2020-02-15 | NOCO ORAS | CLSD | 2020-02-15 |  |  | 22823058 | CM | Complete by 12 Mths | SD006 | A | CP_INS204 | SHUT DOWN VALVE COND TRANS SYS, OKOG1 |  | 2020-03-06 |  | Z1
20200809 | 6 | 11771304 |  | 57SDV912 Solenoid Valve DIS_ALM fault | NG.AFA.OKOG1.ES.57SDV912 | 2020-02-11 | NOCO ORAS | CLSD | 2020-02-11 | 31000136872 |  | 22821883 | CM | Complete by 6 Months | SD005 | A | CP_INS204 | SD VLV, ESD SYS(GRF HP TO LP COND),OKOG1 | ROTORK CP/S-065-250A/A/FB SD VLV | 2020-03-07 |  | Z1
20200809 | 6 | 11771320 |  | 69SDV150 Solenoid Valve DIS_ALM Fault | NG.AFA.OKOG1.ES.69SDV150 | 2020-02-11 | NOCO ORAS | CLSD | 2020-02-11 | 31000136980 |  | 22821884 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(FUEL GAS A-6901),OKOG1 | MAX-AIR UT-55 SD VLV | 2020-03-09 |  | Z1
20190201 | 2 | 11695158 |  | Crossover 33SDV210 Communication failure | NG.AFA.OKOG1.ES.33GIT210 | 2019-01-25 | NOCO ORAS | CLSD | 2019-01-25 |  |  | 22738257 | CM | Complete by 1 Week |  | C | CP_INS202 | GIT, 33SDV210 SD VLV, ESD SYS, OKOG1 |  | 2019-01-29 |  | Z1
20201228 | 3 | 11826406 | X | DIS_ALM On 52SDV120, XHP Flash Drum2 | NG.AFA.OKOG1.ES.52GIT120 | 2020-12-14 | NOPR ORAS | TBCO | 2020-12-14 |  |  | 22887351 | CM | Complete by 2 Weeks |  | C | CP_INS202 | GIT, 52SDV120 SD VLV, ESD SYS, OKOG1 |  |  |  | Z1
20210214 | 5 | 11827378 | X | DIS_ALM on 52SDV340 | NG.AFA.OKOG1.ES.52SDV340 | 2020-12-20 | NOPR ORAS | APPR | 2020-12-20 | 31000136800 |  | 22888729 | CM | Complete by 8 Weeks | SD006 | A | CP_INS204 | SD VLV, ESD SYS(L.P. DRUM 2),OKOG1 | ROTORK CP/S-055-200A/A SD VLV |  |  | Z1
20210214 | 5 | 11827403 |  | DIS_ALM on 53SDV120 | NG.AFA.OKOG1.ES.53SDV120 | 2020-12-20 | NOPR ORAS | APPR | 2020-12-20 | 31000136818 |  | 22888730 | CM | Complete by 8 Weeks | SD006 | A | CP_INS204 | SD VLV, ESD SYS(COND TANK A),OKOG1 | ROTORK CP/S-035-100A/B SD VLV |  |  | Z1
20190317 | 5 | 11694293 |  | DIS_ALM on Shutdown Valves | NG.AFA.OKOG1.ES | 2019-01-20 | NOCO ORAS | CLSD | 2019-01-20 |  |  | 22737527 | CM | Complete by 8 Weeks | SD001 | A | NO_MAINT1 | ESD SYS, OKOG1 |  | 2019-02-05 |  | Z1
20191028 | 6 | 11713654 |  | DIS_ALM/Solenoid valve Fail.on 33SDV210 | NG.AFA.OKOG1.ES.33SDV210 | 2019-05-01 | NOCO ORAS | CLSD | 2019-05-01 | 31000136689 |  | 22758142 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(A-3301 SEP),OKOG1 | ROTORKCP/S045-180A/C+A90R/259MGV900SDV | 2019-10-15 |  | Z1
20191028 | 6 | 11713643 |  | DIS_ALM/Solenoid valve Fail.on 51SDV440 | NG.AFA.OKOG1.ES.51SDV440 | 2019-05-01 | NOCO ORAS | CLSD | 2019-05-01 | 31000136760 |  | 22757200 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(A.P. COND DRUM 1),OKOG1 | ROTORK CP/S-035-100A/B SD VLV | 2019-10-13 |  | Z1
20191027 | 6 | 11713587 |  | DIS_ALM/Solenoid valve Fail.on 52SDV240 | NG.AFA.OKOG1.ES.52SDV240 | 2019-04-30 | NOCO ORAS | CLSD | 2019-04-30 | 31000136794 |  | 22757195 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(H.P. DRUM 2),OKOG1 | ROTORK CP/S-045-140A/B SD VLV | 2019-06-05 |  | Z1
20191027 | 6 | 11713629 |  | DIS_ALM/Solenoid valve Fail.on 52SDV340 | NG.AFA.OKOG1.ES.52SDV340 | 2019-04-30 | NOPR ORAS | APPR | 2019-04-30 | 31000136800 |  | 22757196 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(L.P. DRUM 2),OKOG1 | ROTORK CP/S-055-200A/A SD VLV |  |  | Z1
20190625 | 5 | 11713581 | X | DIS_ALM/Solenoid valve Fail.on 53SDV100 | NG.AFA.OKOG1.ES.53SDV100 | 2019-04-30 | NOCO ORAS | CLSD | 2019-04-30 | 31000136816 |  | 22757197 | CM | Complete by 8 Weeks | SD006 | A | CP_INS204 | SD VLV, ESD SYS(COND TANK A),OKOG1 | ROTORK CP/S-065-335A/C SD VLV | 2019-05-14 |  | Z1
20190625 | 5 | 11713577 | X | DIS_ALM/Solenoid valve Fail.on 53SDV110 | NG.AFA.OKOG1.ES.53EV110 | 2019-04-30 | NOCO ORAS | CLSD | 2019-04-30 |  |  | 22757192 | CM | Complete by 8 Weeks | SD001 | A | CP_INS204 | SOV, 53SDV110 SD VLV, ESD SYS, OKOG1 |  | 2019-05-14 |  | Z1
20191027 | 6 | 11713583 | X | DIS_ALM/Solenoid valve Fail.on 53SDV120 | NG.AFA.OKOG1.ES.53SDV120 | 2019-04-30 | NOCO ORAS | CLSD | 2019-04-30 | 31000136818 |  | 22757198 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(COND TANK A),OKOG1 | ROTORK CP/S-035-100A/B SD VLV | 2019-10-18 |  | Z1
20190625 | 5 | 11713580 | X | DIS_ALM/Solenoid valve Fail.on 53SDV220 | NG.AFA.OKOG1.ES.53SDV220 | 2019-04-30 | NOCO ORAS | CLSD | 2019-04-30 | 31000136821 |  | 22757199 | CM | Complete by 8 Weeks | SD006 | A | CP_INS204 | SD VLV, ESD SYS(COND TANK B),OKOG1 | ROTORK CP/S-035-100A/B SD VLV | 2019-05-16 |  | Z1
20190623 | 5 | 11713131 |  | DIS_ALM/Solenoid valve Fail.on 53SDV301 | NG.AFA.OKOG1.ES.53SDV301 | 2019-04-28 | NOCO ORAS | CLSD | 2019-04-28 | 31000190981 |  | 22756582 | CM | Complete by 8 Weeks | SD001 | A | CP_INS204 | SHUTDWN VLV301, CONDENSATE PPKG-5302, ES | TK MODEL BS6RA74333 SHUTDOWN VALVE | 2019-05-16 |  | Z1
20191027 | 6 | 11713541 |  | DIS_ALM/Solenoid valve Fail.on 53SDV305 | NG.AFA.OKOG1.ES.53SDV305 | 2019-04-30 | NOCO ORAS | CLSD | 2019-04-30 |  |  | 22757194 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SHUT DOWN VALVE COND TRANS SYS, OKOG1 |  | 2019-10-26 |  | Z1
20200428 | 6 | 11751559 |  | Discrepancy alm on V5102 oulet 51SDV210 | NG.AFA.OKOG1.CT.V-5102 | 2019-10-31 | NOCO ORAS | CLSD | 2019-10-31 | 31000137332 |  | 22794624 | CM | Complete by 6 Months | PC001 | A | CP_STA506 | HP COND F/DRM 2, COND TRANS SYS, OKOG1 | IDESA HP COND F/DRM 2 | 2019-11-17 |  | Z1
20210129 | 6 | 11801250 | X | 51SDV121 solenoid valve regulat Air leak | NG.AFA.OKOG1.ES.51SDV121 | 2020-08-02 | NOPR ORAS | APPR | 2020-08-02 | 31000136747 |  | 22862071 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(XHP DRUM 1),OKOG1 | ROTORKCP/S065-280A/B+A90R/259MGV900SDV |  |  | Z1
20200801 | 6 | 11769806 |  | Air regulator leaks on 53SDV220 | NG.AFA.OKOG1.ES.53SDV220 | 2020-02-03 | NOCO ORAS | CLSD | 2020-02-03 | 31000136821 |  | 22819737 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(COND TANK B),OKOG1 | ROTORK CP/S-035-100A/B SD VLV | 2020-05-19 |  | Z1
20210117 | 4 | 11827401 |  | Instrument Air leak from 56SDV1003 | NG.AFA.OKOG1.ES.56SDV1003 | 2020-12-20 | NOPR ORAS | APPR | 2020-12-20 |  |  | 22888727 | CM | Complete by 4 Weeks | SD006 | A | CP_INS204 | SHUT DOWN VALVE, ESD SYS,OKOG1 |  |  |  | Z1
20200704 | 6 | 11763973 |  | Faulty regulator on 12SDV110 Slug Catche | NG.AFA.OKOG1.ES.12SDV110 | 2020-01-06 | NOCO ORAS | CLSD | 2020-01-06 | 31000136619 |  | 22810586 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(V-1201),OKOG1 | ROTORKCP/S065-280A/B+A90R/259MGV900SDV | 2020-05-13 |  | Z1
20201013 | 3 | 11812273 |  | Faulty regulator on 57SDV920 at GRF | NG.AFA.OKOG1.ES.57SDV920 | 2020-09-29 | NOCO ORAS | CLSD | 2020-09-29 | 31000136873 |  | 22871914 | CM | Complete by 2 Weeks | SD005 | A | CP_INS204 | SD VLV, ESD SYS(GRF HP TO LP COND),OKOG1 | SHUTDOWN VALVE | 2020-10-10 |  | Z1
20190423 | 6 | 11677260 |  | Leaking air from 10SDV120 on W/27T inlet | NG.AFA.OKOG1.ES.10SDV120 | 2018-10-25 | NOCO ORAS | CLSD | 2018-10-25 | 31000175281 |  | 22700168 | CM | Complete by 6 Months |  | B | CP_INS204 | SHUTDOWN VALVE,SWING WELL PIG RECV,OKOG1 | SHUTDOWN VALVE,SWING WELL PIG RECEIVER | 2019-07-14 |  | Z1
20180317 | 5 | 11618584 |  | Leaking air from 10SDV120 on W/27T line | NG.AFA.OKOG1.ES.10SDV120 | 2018-01-20 | NOCO ORAS | CLSD | 2018-01-20 | 31000175281 |  | 22632034 | CM | Complete by 8 Weeks |  | B | CP_INS202 | SHUTDOWN VALVE,SWING WELL PIG RECV,OKOG1 | SHUTDOWN VALVE,SWING WELL PIG RECEIVER | 2018-03-07 |  | Z1
20180815 | 2 | 11662672 |  | Rectify Instrument air leak on 57SDV908 | NG.AFA.AFAG2.ES.57SDV908 | 2018-08-08 | NOCO ORAS | CLSD | 2018-08-08 |  |  | 22681697 | CM | Complete by 1 Week | SD006 | A | CP_INS204 | SDV, MAIN INLET 1, GAS SEP SYS, AFAM GRF |  | 2018-08-13 |  | Z1
20211022 | 7 | 11817087 |  | Volme booster on 53SDV304 air leaking | NG.AFA.OKOG1.ES | 2020-10-27 | NOCO ORAS | CLSD | 2020-10-27 |  |  | 22879746 | CM | Complete by 12 Mths | SD001 | A | NO_MAINT1 | ESD SYS, OKOG1 |  | 2020-11-27 |  | Z1
20190513 | 4 | 11710298 |  | W24 SDV 09SDV110 IA Regulator leaking | NG.AFA.OKOG1.FL.AFAM WELL 24T | 2019-04-15 | NOCO ORAS | CLSD | 2019-04-15 |  |  | 22753144 | CM | Complete by 4 Weeks | PC006 | A | CP_STA504 | TANGO STRING FLOWLINE, WELL 24, OKOLOMA |  | 2019-04-26 |  | Z1
20190920 | 6 | 11706265 |  | 53SDV301 Solenoid valve failed | NG.AFA.OKOG1.ES.53EV301 | 2019-03-24 | NOCO ORAS | CLSD | 2019-03-24 |  |  | 22748878 | CM | Complete by 6 Months |  | B | CP_INS204 | SOLENOID VLV301, CONDENSATE PPKG5302, ES |  | 2019-08-28 |  | Z1
20191229 | 4 | 11757687 |  | faulty valve actuactor | NG.AFA.OKOG1.ES | 2019-12-01 | NOCO ORAS | CLSD | 2019-12-01 |  |  | 22801494 | CM | Complete by 4 Weeks | SD001 | A | NO_MAINT1 | ESD SYS, OKOG1 |  | 2020-01-08 |  | Z1
20200628 | 6 | 11763037 | X | 45BDV200 found passing | NG.AFA.OKOG1.ES.45EV200 | 2019-12-31 | NOCO ORAS | CLSD | 2019-12-31 |  |  | 22808965 | CM | Complete by 6 Months | SD001 | A | CP_INS204 | SOV, 45BDV200 BDV, ESD SYS, OKOG1 |  | 2020-01-18 |  | Z1
20180829 | 4 | 11661236 |  | EPAF 62SDV931 Stuck open | NG.AFA.OKOG1.ES.62SDV931 | 2018-08-01 | NOCO ORAS | CLSD EPAF | 2018-08-01 | 31000136889 |  | 22680043 | CM | Complete by 4 Weeks | SD006 | A | CP_INS204 | SD VLV, ESD SYS(FIRE WATER DIST),OKOG1 | ROTORK CP/S-045-140A/B/FB SD VLV | 2018-08-27 | 50000024 | Z1
20200713 | 6 | 11765728 | X | cond strg Tank A (53SDV110) stuck closed | NG.AFA.OKOG1.CT.T-5301A | 2020-01-15 | NOCO ORAS | CLSD | 2020-01-15 | 31000137289 |  | 22812596 | CM | Complete by 6 Months | PC004 | A | CP_STA505 | COND STR TNK A, COND TRANS SYS, OKOG1 | NIGERDOCK NIGERIA COND STR TNK A | 2020-02-16 |  | Z1
20200403 | 6 | 11746149 |  | 51SDV121 stuck in open/close position | NG.AFA.OKOG1.ES.51SDV121 | 2019-10-06 | NOCO ORAS | CLSD | 2019-10-06 | 31000136747 |  | 22788175 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(XHP DRUM 1),OKOG1 | ROTORKCP/S065-280A/B+A90R/259MGV900SDV | 2020-02-11 |  | Z1
20190104 | 3 | 11688588 | X | 52BDV330 stucked open at LP DRUM2 | NG.AFA.OKOG1.ES.52BDV330 | 2018-12-21 | NOCO ORAS | CLSD | 2018-12-21 | 31000136766 |  | 22714171 | CM | Complete by 2 Weeks | SD002 | A | CP_INS204 | BDV, ESD SYS(L.P. DRUM 2),OKOG1 | ROTORK CP/S-045-120A/A BDV | 2018-12-26 |  | Z1
20190517 | 6 | 11682089 |  | 52SDV241 stucked open at HP DRUM2 | NG.AFA.OKOG1.ES.52SDV241 | 2018-11-18 | NOCO ORAS | CLSD | 2018-11-18 | 31000136795 |  | 22706204 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(H.P. DRUM 2),OKOG1 | ROTORKCP/S065-280A/B+A90R/259MGV900SDV | 2018-11-24 |  | Z1
20200115 | 3 | 11763192 | X | 57SDV911 stuck closed, LIQ OUTLET GRF | NG.AFA.AFAG2.ES.57SDV911 | 2020-01-01 | NOCO ORAS | CLSD | 2020-01-01 |  |  | 22809250 | CM | Complete by 2 Weeks | SD006 | A | CP_INS204 | SDV,LIQ OUTLET V4602 GAS SEP SYS,AFAMGRF |  | 2020-01-08 |  | Z1
20191217 | 5 | 11749744 |  | stucked/limited movement in valves at ES | NG.AFA.OKOG1.ES | 2019-10-22 | NOCO ORAS | CLSD | 2019-10-22 |  |  | 22791981 | CM | Complete by 8 Weeks | SD001 | A | NO_MAINT1 | ESD SYS, OKOG1 |  | 2019-12-12 |  | Z1
20200108 | 4 | 11759025 | X | Unit 52 SDV-121 not closing fully | NG.AFA.OKOG1.ES.52SDV121 | 2019-12-11 | NOCO NOPT ORAS | CLSD | 2019-12-11 | 31000136790 |  | 22804421 | CM | Complete by 4 Weeks | SD006 | A | CP_INS204 | SD VLV, ESD SYS(XHP DRUM 2),OKOG1 | ROTORKCP/S-045-180/C-A90R/259MGV900SDV | 2019-12-24 |  | Z1
20201009 | 6 | 11782248 |  | XXHP 52SDV511 stuck in closed position | NG.AFA.OKOG1.ES.52SDV511 | 2020-04-12 | NOCO ORAS | CLSD | 2020-04-12 | 31000180777 |  | 22837709 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SHUTDOWN VALVE1,XXHP SEPARATOR,OKOG1 | CAMERON LEEDEN TYPE-BALL/66616SRC8 VALVE | 2020-07-15 |  | Z1
20201005 | 6 | 11781825 |  | Twister 32KSV005 stuck in closed positn | NG.AFA.OKOG1.ES.32KSV005 | 2020-04-08 | NOCO ORAS | CLSD | 2020-04-08 | 31000136648 |  | 22836465 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(TWISTER PACKAGE),OKOG1 | MOKVELD RZD-X SD VLV | 2020-04-21 |  | Z1
20180214 | 3 | 11620843 |  | EPAF ESD Valve operates incorrectly (positioner) | NG.AFA.OKOG1.ES.32KSV600 | 2018-01-31 | NOCO ORAS | CLSD EPAF | 2018-01-31 | 31000136659 |  | 22635726 | CM | Complete by 2 Weeks | SD006 | A | CP_INS204 | SD VLV, ESD SYS(TWISTER PACKAGE),OKOG1 | MOKVELD RZD-X SD VLV | 2018-02-19 | 50000024 | Z1
20190606 | 6 | 11686154 |  | 10KSV900 failed on demand at RM (positioner) | NG.AFA.OKOG1.ES.10KSV900 | 2018-12-08 | NOCO ORAS | CLSD | 2018-12-08 |  |  | 22711258 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(WELL F10F14-22),OKOG1 |  | 2019-06-03 |  | Z1
20190919 | 4 | 11736261 | X | Failure of 52BDV500, XXHP Separator (Positioner) | NG.OKOG1.V-5205-52GIT500 | 2019-08-22 | NOCO ORAS | CLSD | 2019-08-22 |  |  | 22779120 | CM | Complete by 4 Weeks |  | A | CP_INS204 | VLV PSTN TRANSMITR2,XXHP SEPARATOR,OKOG1 |  | 2019-09-11 |  | Z1
20190910 | 4 | 11734222 |  | Failure of 52SDV120, XHP Drum 2 (positioner) | NG.AFA.OKOG1.ES.52GIT120 | 2019-08-13 | NOCO ORAS | CLSD | 2019-08-13 |  |  | 22777283 | CM | Complete by 4 Weeks |  | C | CP_INS202 | GIT, 52SDV120 SD VLV, ESD SYS, OKOG1 |  | 2019-08-22 |  | Z1
20201115 | 2 | 11819191 |  | FGC 56BDV200 valve failure (positioner) | NG.AFA.OKOG1.ES.56BDV200 | 2020-11-08 | NOPR ORAS | TBCO | 2020-11-08 | 31000136823 |  | 22879745 | CM | Complete by 1 Week | SD002 | A | CP_INS204 | BDV, ESD SYS(F GAS COMP),OKOG1 | ORSENIGO FB2 BDV |  |  | Z1
20190603 | 5 | 11709025 |  | EPAF ESD Valve closure time (slow response) | NG.AFA.OKOG1.ES.51SDV242 | 2019-04-08 | NOCO ORAS | CLSD EPAF | 2019-04-08 | 31000136753 |  | 22752230 | CM | Complete by 8 Weeks | SD006 | A | CP_INS204 | SD VLV, ESD SYS(COND HEATER 1),OKOG1 | ROTORK CP/S-045-140/B SD VLV | 2019-05-14 | 50000025 | Z1
20210206 | 5 | 11826102 | X | EPAF ESD Valve closure time (actuator) | NG.AFA.OKOG1.ES.69SDV110 | 2020-12-12 | NOPR ORAS | APPR EPAF | 2020-12-12 | 31000136978 |  | 22887353 | CM | Complete by 8 Weeks | SD006 | A | CP_INS204 | SD VLV, ESD SYS(FUEL GAS A-6901),OKOG1 | FISHERS FISHER/STAR SD VLV |  | 50000025 | Z1
20191005 | 6 | 11709026 |  | EPAF ESD Valve operates correctly (slow response) | NG.AFA.OKOG1.ES.51SDV242 | 2019-04-08 | NOCO ORAS | CLSD EPAF | 2019-04-08 | 31000136753 |  | 22752231 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(COND HEATER 1),OKOG1 | ROTORK CP/S-045-140/B SD VLV | 2019-05-13 | 50000024 | Z1
20200103 | 5 | 11753152 |  | 51SDV140 leaking from over pres. nipple | NG.AFA.OKOG1.ES.51SDV140 | 2019-11-08 | NOCO ORAS | CLSD | 2019-11-08 | 31000180778 |  | 22797136 | CM | Complete by 8 Weeks | SD006 | A | CP_INS204 | SHUTDOWN VALVE2,XXHP SEPARATOR,OKOG1 | DELLA FOGLIA/BIFFI,TN/0.9C-0700-385,SDV2 | 2020-01-02 |  | Z1
20210203 | 5 | 11825403 |  | 51SDV140 weeping from greasing nipple | NG.OKOG1.V-5205-51GIT140 | 2020-12-09 | NOPR ORAS | APPR | 2020-12-09 |  |  | 22889022 | CM | Complete by 8 Weeks |  | A | CP_INS204 | VLV PSTN TRANSMITR3,XXHP SEPARATOR,OKOG1 |  |  |  | Z1
20191224 | 4 | 11756607 |  | 4th stg Train1 dis v/v, 56SDV372, faulty (leaking nipple) | NG.AFA.HBA.OKOG1-SHUTDOWN_SYSTEM | 2019-11-25 | NOCO ORAS | CLSD | 2019-11-26 |  |  | 22800386 | CM | Complete by 4 Weeks |  | A | NO_MAINT1 | OKOLOMA G/P SHUTDOWN SYSTEM |  | 2019-12-21 |  | Z1
20191215 | 5 | 11749131 |  | 45SDV907 failed in operation-SD Activity | NG.AFA.OKOG1.PL.A-4592A | 2019-10-20 | NOCO ORAS | CLSD | 2019-10-20 |  |  | 22791980 | CM | Complete by 8 Weeks | PC006 | A | CP_STA504 | SALES GAS PIG/L, PIG L/R SYS, OKOG1 |  | 2019-12-09 |  | Z1
20200403 | 6 | 11746148 |  | 51SDV120 fails to open/close on demand | NG.AFA.OKOG1.ES.51SDV120 | 2019-10-06 | NOCO ORAS | CLSD | 2019-10-06 | 31000136746 |  | 22787893 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(XHP DRUM 1),OKOG1 | ROTORKCP/S065-280A/B+A90R/259MGV900SDV | 2019-12-22 |  | Z1
20190829 | 6 | 11702344 |  | 51SDV242 fail to close on time | NG.AFA.OKOG1.ES.51SDV242 | 2019-03-02 | NOCO ORAS | CLSD | 2019-03-02 | 31000136753 |  | 22743707 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(COND HEATER 1),OKOG1 | ROTORK CP/S-045-140/B SD VLV | 2019-08-18 |  | Z1
20190427 | 5 | 11702324 |  | 52BDV430 fail to close on demand | NG.AFA.OKOG1.ES.52BDV430 | 2019-03-02 | NOCO ORAS | CLSD | 2019-03-02 | 31000136767 |  | 22743314 | CM | Complete by 8 Weeks | SD002 | A | CP_INS204 | BDV, ESD SYS(A.P. DRUM 2),OKOG1 | ROTORK CP/S-055-200A/B BDV | 2019-03-06 |  | Z1
20210208 | 5 | 11826412 | X | 52SDV110 failed to open, XHP Drum2 | NG.AFA.OKOG1.ES.52GIT110 | 2020-12-14 | NOPR ORAS | APPR | 2020-12-14 |  |  | 22888728 | CM | Complete by 8 Weeks |  | C | CP_INS202 | GIT, 52SDV110 SD VLV, ESD SYS, OKOG1 |  |  |  | Z1
20200403 | 6 | 11746151 |  | 52SDV121 Fail to open or close on demand | NG.AFA.OKOG1.ES.52SDV121 | 2019-10-06 | NOCO ORAS | CLSD | 2019-10-06 | 31000136790 |  | 22788176 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(XHP DRUM 2),OKOG1 | ROTORKCP/S-045-180/C-A90R/259MGV900SDV | 2019-10-25 |  | Z1
20180523 | 4 | 11639548 | X | 52SDV400 failed to open at AP DRUM 2 | NG.AFA.OKOG1.ES.52EV400 | 2018-04-25 | NOCO ORAS | CLSD | 2018-04-25 |  |  | 22656564 | CM | Complete by 4 Weeks | SD001 | A | CP_INS204 | SOV, 52SDV400 SD VLV, ESD SYS, OKOG1 |  | 2018-05-04 |  | Z1
20180502 | 5 | 11629169 |  | 52SDV400 failed to open on demand | NG.AFA.OKOG1.ES.52GIT400 | 2018-03-07 | NOCO ORAS | CLSD | 2018-03-07 |  |  | 22644223 | CM | Complete by 8 Weeks |  | C | CP_INS202 | GIT, 52SDV400 SD VLV, ESD SYS, OKOG1 |  | 2018-03-30 |  | Z1
20200403 | 6 | 11746150 |  | 56SDV210 Fail to open or close on demand | NG.AFA.OKOG1.ES.56SDV210 | 2019-10-06 | NOCO ORAS | CLSD | 2019-10-06 | 31000136855 |  | 22788177 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(F GAS COMP),OKOG1 | ORSENIGO FB2 SD VLV | 2019-11-20 |  | Z1
20201101 | 4 | 11813029 | X | 69SDV110 failed to respond | NG.AFA.OKOG1.ES.69SDV110 | 2020-10-04 | NOPR ORAS | APPR | 2020-10-04 | 31000136978 |  | 22872413 | CM | Complete by 4 Weeks | SD006 | A | CP_INS204 | SD VLV, ESD SYS(FUEL GAS A-6901),OKOG1 | FISHERS FISHER/STAR SD VLV |  |  | Z1
20190525 | 5 | 11707355 |  | Integrity chks required on 45SDV001 GRF | NG.AFA.AFAG2.ES.45SDV001 | 2019-03-30 | NOCO ORAS | CLSD | 2019-03-30 | 31000101144 |  | 22749826 | CM | Complete by 8 Weeks | SD006 | A | CP_INS204 | SHUTDOWN VLV,INLET MANIFOLD SYS,AFAM GRF | VALVITALIA,LPS-13-640-CM30-FC,6"X300#SDV | 2019-04-13 |  | Z1
20200308 | 4 | 11770913 |  | Oil Test Sep. 50SDV120 failed to reset | NG.AFA.OKOG1.ES.50SDV120 | 2020-02-09 | NOCO ORAS | CLSD | 2020-02-09 | 31000136718 |  | 22821625 | CM | Complete by 4 Weeks | SD006 | A | CP_INS204 | SD VLV, ESD SYS(OIL TEST SEP),OKOG1 | AIR TORQUE/FCTAT551 F10AF14-ND-36LTSDV | 2020-02-24 |  | Z1
20190208 | 3 | 11695145 |  | Slug catcher 11SDV110 failed on demand | NG.AFA.OKOG1.ES.11EV110 | 2019-01-25 | NOCO ORAS | CLSD | 2019-01-25 |  |  | 22738256 | CM | Complete by 2 Weeks | SD001 | A | CP_INS204 | SOV, 11SDV110 SD VLV, ESD SYS, OKOG1 |  | 2019-02-05 |  | Z1
20200322 | 5 | 11768302 | X | Blow Down V/v Failure- 52BDV330 LP Unt52 | NG.AFA.OKOG1.ES.52BDV330 | 2020-01-26 | NOCO ORAS | CLSD | 2020-01-26 | 31000136766 |  | 22816010 | CM | Complete by 8 Weeks | SD002 | A | CP_INS204 | BDV, ESD SYS(L.P. DRUM 2),OKOG1 | ROTORK CP/S-045-120A/A BDV | 2020-03-12 |  | Z1
20180708 | 6 | 11616357 | X | Failure of 32KSV600 Tube 6 Inlet KSV | NG.AFA.OKOG1.ES.32EV600 | 2018-01-09 | NOCO ORAS | CLSD | 2018-01-09 |  |  | 22629387 | CM | Complete by 6 Months | SD001 | A | CP_INS204 | SOV, 32KSV600 SD VLV, ESD SYS, OKOG1 |  | 2018-07-09 |  | Z1
20201204 | 6 | 11791395 |  | Tube 6 32KSV601 module suspected faulty (power Module) | NG.AFA.OKOG1.ES.32KSV601 | 2020-06-07 | NOCO ORAS | CLSD | 2020-06-07 | 31000136660 |  | 22849585 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(TWISTER PACKAGE),OKOG1 | ORSENIGO FB BALL VALVE SD VLV | 2020-06-15 |  | Z1
20200807 | 6 | 11770925 |  | Twister Tube 3 Outlet 32KSV301 faulty (MOD_BAD) | NG.AFA.OKOG1.GS.S-3230 | 2020-02-09 | NOCO ORAS | CLSD | 2020-02-09 | 31000137264 |  | 22821628 | CM | Complete by 6 Months |  | A | CP_STA506 | TWST TUBE 30, GAS SEP SYS, OKOG1 | NEM BV TWST TUBE 30 | 2020-04-04 |  | Z1
20190625 | 6 | 11689457 | X | 32KSV300/MOD_BAD on Tube 3 TWSITER Pkg | NG.AFA.OKOG1.ES.32KSV300 | 2018-12-27 | NOCO ORAS | CLSD | 2018-12-27 | 31000136653 |  | 22715177 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(TWISTER PACKAGE),OKOG1 | MOKVELD RZD-X SD VLV | 2019-03-05 |  | Z1
20190625 | 6 | 11689459 |  | 32KSV400/MOD_BAD on Tube 4 TWSITER Pkg | NG.AFA.OKOG1.ES.32KSV400 | 2018-12-27 | NOCO ORAS | CLSD | 2018-12-27 | 31000136655 |  | 22715178 | CM | Complete by 6 Months | SD006 | A | CP_INS204 | SD VLV, ESD SYS(TWISTER PACKAGE),OKOG1 | MOKVELD RZD-X SD VLV | 2019-03-08 |  | Z1
20200223 | 5 | 11762749 | X | MOD_BAD ALM on 32KSV301 TUBE3 Outlet | NG.AFA.OKOG1.ES.32KSV301 | 2019-12-29 | NOCO ORAS | CLSD | 2019-12-29 | 31000136654 |  | 22808522 | CM | Complete by 8 Weeks | SD006 | A | CP_INS204 | SD VLV, ESD SYS(TWISTER PACKAGE),OKOG1 | ORSENIGO FB BALL VALVE SD VLV | 2020-01-15 |  | Z1
20210611 | 6 | 11826192 |  | PV_BAD alarm on 51BDV131 | NG.AFA.OKOG1.ES.51BDV131 | 2020-12-13 | NOPR ORAS | APPR | 2020-12-13 | 31000136721 |  | 22887356 | CM | Complete by 6 Months | SD002 | A | CP_INS204 | BDV, ESD SYS(XHP DRUM 1),OKOG1 | ROTORK CP/S-055-160A/A BDV |  |  | Z1
20201213 | 5 | 11815363 |  | Spurious MOD_BAD alarm on 32KSV400 | NG.AFA.OKOG1.ES.32KSV400 | 2020-10-18 | NOCO ORAS | CLSD | 2020-10-18 | 31000136655 |  | 22875010 | CM | Complete by 8 Weeks | SD006 | A | CP_INS204 | SD VLV, ESD SYS(TWISTER PACKAGE),OKOG1 | MOKVELD RZD-X SD VLV | 2020-11-12 |  | Z1
20190927 | 6 | 11707387 |  | Config. of ESD Criteria on DCS | NG.AFA.OKOG1.ES | 2019-03-31 | NOCO ORAS | CLSD | 2019-03-31 |  |  | 22750030 | CM | Complete by 6 Months | SD001 | A | NO_MAINT1 | ESD SYS, OKOG1 |  | 2019-09-07 |  | Z1
20210430 | 6 | 11817921 |  | Drain v/v 09BV001 gasket & bolts rusted | NG.AFA.OKOG1.FL.AFAM WELL 24T | 2020-11-01 | NOPR ORAS | APPR | 2020-11-01 |  |  | 22880842 | CM | Complete by 6 Months | PC006 | A | CP_STA504 | TANGO STRING FLOWLINE, WELL 24, OKOLOMA |  |  |  | Z1
20200223 | 3 | 11770899 | X | 50SDV140 Failed to reset | NG.AFA.OKOG1.ES.50SDV140 | 2020-02-09 | NOCO ORAS | CLSD | 2020-02-09 | 31000136719 |  | 22820856 | CM | Complete by 2 Weeks | SD006 | A | CP_INS204 | SD VLV, ESD SYS(OIL TEST SEP),OKOG1 | AIR TORQUE/FCT AT701S10AF16-N-D-36SDV | 2020-02-18 |  | Z1

## WO
Main work center | Order | Basic start date | ABC indicator | Scheduled finish | Latest Allowed Finish Date | User Status | System status | Description | FunctLocDescrip. | Functional Location | Scheduled start | Original Latest Allowed Finish Date | Actual Finish Date | Order Type | Priority | Equipment | Created on | Basic finish date | Actual start date | Group | Group Counter | Maintenance item | Maintenance Plan | Cost Center | Object Description | Assembly desc. | Execution Condition | Long text exists | Notification | Object list | Priority type | PO Number | System Condition | Total planned costs | Estimated costs | Total actual costs
AFAINST | 22743314 | 2019-03-05 | A | 2019-03-05 | 2019-04-27 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Rectify 52BDV430 fail to close | BDV, ESD SYS(A.P. DRUM 2),OKOG1 | NG.AFA.OKOG1.ES.52BDV430 | 2019-03-05 | 2019-04-27 | 2019-03-05 | 72FC | 5 | 31000136767 | 2019-03-03 | 2019-03-05 | 2019-03-05 | [5 empty] | ROTORK CP/S-055-200A/B BDV |  | ONTR | E | 11702324 | 809708 | CM |  | 0 | 1056.4 | 1056.4 | 1056.4
AFAINST | 22879745 | 2020-11-13 | A | 2020-11-13 | 2020-11-15 | XCNF XGI | TECO CNF ESTC NMAT PRC SETC | Rectify FGC 56BDV200 valve failure | BDV, ESD SYS(F GAS COMP),OKOG1 | NG.AFA.OKOG1.ES.56BDV200 | 2020-11-13 | 2020-11-15 | 2020-11-15 | 72FC | 2 | 31000136823 | 2020-11-12 | 2020-11-13 | 2020-11-13 | [5 empty] | ORSENIGO FB2 BDV |  | ONTR |  | 11819191 | 916222 | CM |  | 0 | 1520 | 1520 | 0
AFAINST | 22714171 | 2018-12-26 | A | 2018-12-26 | 2019-01-04 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Service 52BDV330 stucked open at LP DRUM | BDV, ESD SYS(L.P. DRUM 2),OKOG1 | NG.AFA.OKOG1.ES.52BDV330 | 2018-12-26 | 2019-01-04 | 2018-12-26 | 72FC | 3 | 31000136766 | 2018-12-22 | 2018-12-26 | 2018-12-26 | [5 empty] | ROTORK CP/S-045-120A/A BDV | ROTORK CP/S-045-120A/A BDV | ONTR | E | 11688588 | 794353 | CM |  | 0 | 912 | 912 | 912
AFAINST | 22666312 | 2018-11-12 | A | 2018-11-13 | 2019-06-02 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Stop Inst Air leak on 53SDV305 at 18K pu | CONDENSATE PUMP PACKAGE 5302, OKOG1 | NG.AFA.OKOG1.CT.P-5302 | 2018-11-12 | 2019-06-02 | 2018-11-13 | 72FC | 7 |  | 2018-06-08 | 2018-11-13 | 2018-11-12 | [7 empty] | ONTR | E | 11650051 | 757565 | CM |  | 0 | 1938 | 1938 | 1938
AFAINST | 22791981 | 2019-11-27 | A | 2019-12-02 | 2019-12-17 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Servicing of stucked SDVs at OKGP | ESD SYS, OKOG1 | NG.AFA.OKOG1.ES | 2019-11-27 | 2019-12-17 | 2019-12-09 | 72FC | 5 |  | 2019-10-23 | 2019-12-02 | 2019-11-27 | [7 empty] | SDTA | E | 11749744 | 850923 | CM |  | 0 | 8512 | 10032 | 456
AFAINST | 22887351 | 2020-12-21 | C | 2020-12-21 | 2020-12-28 | XCNF XGI | TECO CNF ESTC NMAT PRC SETC | Rectify DIS_ALM On 52SDV120, XHP Drum2 | GIT, 52SDV120 SD VLV, ESD SYS, OKOG1 | NG.AFA.OKOG1.ES.52GIT120 | 2020-12-21 | 2020-12-28 | 2020-12-21 | 72FC | 3 |  | 2020-12-16 | 2020-12-21 | 2020-12-21 | [7 empty] | ONTR |  | 11826406 | 923276 | CM |  | 0 | 760 | 760 | 760
AFAINST | 22777283 | 2019-08-21 | C | 2019-08-21 | 2019-09-10 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Rectify Failure of 52SDV120, XHP Drum 2 | GIT, 52SDV120 SD VLV, ESD SYS, OKOG1 | NG.AFA.OKOG1.ES.52GIT120 | 2019-08-21 | 2019-09-10 | 2019-08-22 | 72FC | 4 |  | 2019-08-15 | 2019-08-21 | 2019-08-21 | [7 empty] | ONTR | E | 11734222 | 838679 | CM |  | 0 | 912 | 912 | 912
AFAINST | 22644223 | 2018-03-30 | C | 2018-03-30 | 2018-05-02 | XCNF XGI | CLSD CNF CSER NMAT PRC SETC | Rectify cause of 52SDV400 failure to ope | GIT, 52SDV400 SD VLV, ESD SYS, OKOG1 | NG.AFA.OKOG1.ES.52GIT400 | 2018-03-30 | 2018-05-02 | 2018-03-30 | 72FC | 5 |  | 2018-03-09 | 2018-03-30 | 2018-03-30 | [7 empty] | ONTR | E | 11629169 | 739504 | CM |  | 0 | 0 | 0 | 646
AFAINST | 22794624 | 2019-11-17 | A | 2019-11-17 | 2020-04-28 | XCNF XGI | CLSD CNF NMAT PRC SETC | Discrepancy alm on V5102 oulet 51SDV210 | HP COND F/DRM 2, COND TRANS SYS, OKOG1 | NG.AFA.OKOG1.CT.V-5102 | 2019-11-17 | 2020-04-28 | 2019-11-17 | 72FC | 6 | 31000137332 | 2019-11-02 | 2019-11-17 | 2019-11-17 | [5 empty] | IDESA HP COND F/DRM 2 |  | ONTR | E | 11751559 | 852843 | CM |  | 0 | 570 | 570 | 570
AFAINST | 22769502 | 2019-07-15 | B | 2019-07-15 | 2019-08-04 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Rectify DIS_ALM on 56SDV210/Failure | LCV, V-5602, GAS COMPR SYS, OKOG1 | NG.OKOG1.V-5602-56LCV200 | 2019-07-15 | 2019-08-04 | 2019-07-15 | 72FC | 4 | 31000136827 | 2019-07-07 | 2019-07-15 | 2019-07-15 | [5 empty] | FISHERS LEVEL CONTROL VALVE |  | ONTR | E | 11727019 | 832157 | CM |  | 0 | 608 | 608 | 608
AFAINST | 22800386 | 2019-12-19 | A | 2019-12-19 | 2019-12-24 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | 4th stg Train1 dis v/v, 56SDV372, faulty | OKOLOMA G/P SHUTDOWN SYSTEM | NG.AFA.HBA.OKOG1-SHUTDOWN_SYSTEM | 2019-12-19 | 2019-12-24 | 2019-12-19 | 72FC | 4 |  | 2019-11-27 | 2019-12-19 | 2019-12-19 | [7 empty] | SDTA |  | 11756607 | 856972 | CM |  | 0 | 722 | 722 | 722
AFAINST | 22791980 | 2019-12-05 | A | 2019-12-05 | 2019-12-15 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Carry out repairs on 45SDV907 failed in | SALES GAS PIG/L, PIG L/R SYS, OKOG1 | NG.AFA.OKOG1.PL.A-4592A | 2019-12-05 | 2019-12-15 | 2019-12-05 | 72FC | 5 |  | 2019-10-23 | 2019-12-05 | 2019-12-05 | [7 empty] | SDTA | E | 11749131 | 850921 | CM |  | 0 | 836 | 836 | 836
AFAINST | 22757200 | 2019-10-13 | A | 2019-10-13 | 2019-10-28 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | RESOLVE DIS_ALM/Solenoid valve Fail.on 5 | SD VLV, ESD SYS(A.P. COND DRUM 1),OKOG1 | NG.AFA.OKOG1.ES.51SDV440 | 2019-10-13 | 2019-10-28 | 2019-10-13 | 72FC | 6 | 31000136760 | 2019-05-03 | 2019-10-13 | 2019-10-13 | [5 empty] | ROTORK CP/S-035-100A/B SD VLV |  | ONTR | E | 11713643 | 820801 | CM |  | 0 | 1064 | 1064 | 1064
AFAINST | 22758142 | 2019-10-15 | A | 2019-10-15 | 2019-10-28 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Resolve DIS_ALM/Solenoid valve Fail.on 3 | SD VLV, ESD SYS(A-3301 SEP),OKOG1 | NG.AFA.OKOG1.ES.33SDV210 | 2019-10-15 | 2019-10-28 | 2019-10-15 | 72FC | 6 | 31000136689 | 2019-05-05 | 2019-10-15 | 2019-10-15 | [5 empty] | ROTORKCP/S045-180A/C+A90R/259MGV900SDV |  | ONTR | E | 11713654 | 821360 | CM |  | 0 | 760 | 760 | 760
AFAINST | 22743707 | 2019-08-16 | A | 2019-08-14 | 2019-08-29 | XCNF XGI | CLSD CNF ESTC NMAT NTUP PRC SETC | Rectify 51SDV242 failure to close on tim | SD VLV, ESD SYS(COND HEATER 1),OKOG1 | NG.AFA.OKOG1.ES.51SDV242 | 2019-08-14 | 2019-08-29 | 2019-08-18 | 72FC | 6 | 31000136753 | 2019-03-05 | 2019-08-19 | 2019-08-14 | [5 empty] | ROTORK CP/S-045-140/B SD VLV |  | ONTR | E | 11702344 | 809982 | CM |  | 0 | 760 | 760 | 684
AFAINST | 22752230 | 2019-05-14 | A | 2019-05-14 | 2019-06-03 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Rectify valve with slow closure time | SD VLV, ESD SYS(COND HEATER 1),OKOG1 | NG.AFA.OKOG1.ES.51SDV242 | 2019-05-14 | 2019-06-03 | 2019-05-14 | 72FC | 5 | 31000136753 | 2019-04-10 | 2019-05-14 | 2019-05-14 | [5 empty] | ROTORK CP/S-045-140/B SD VLV |  | ONTR | E | 11709025 | 816940 | CM |  | 0 | 684 | 684 | 684
AFAINST | 22752231 | 2019-05-11 | A | 2019-05-11 | 2019-10-05 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | RECTIFY ESD VALVE NOT OPERATING CORRECTL | SD VLV, ESD SYS(COND HEATER 1),OKOG1 | NG.AFA.OKOG1.ES.51SDV242 | 2019-05-11 | 2019-10-05 | 2019-05-11 | 72FC | 6 | 31000136753 | 2019-04-10 | 2019-05-11 | 2019-05-11 | [5 empty] | ROTORK CP/S-045-140/B SD VLV |  | ONTR | E | 11709026 | 816941 | CM |  | 0 | 820.8 | 820.8 | 820.8
AFAINST | 22757197 | 2019-05-14 | A | 2019-05-14 | 2019-06-25 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | RESOLVE Solenoid valve Fail.on 53SDV100 | SD VLV, ESD SYS(COND TANK A),OKOG1 | NG.AFA.OKOG1.ES.53SDV100 | 2019-05-14 | 2019-06-25 | 2019-05-14 | 72FC | 5 | 31000136816 | 2019-05-03 | 2019-05-14 | 2019-05-14 | [5 empty] | ROTORK CP/S-065-335A/C SD VLV |  | ONTR | E | 11713581 | 820798 | CM |  | 0 | 1178 | 1178 | 1178
AFAINST | 22884395 | 2020-12-22 | A | 2020-12-23 | 2020-12-30 | XCNF XGI | TECO CNF ESTC NMAT PRC SETC | Rectify 53SDV110 INCESSANT FAILURE/DIS_A | SD VLV, ESD SYS(COND TANK A),OKOG1 | NG.AFA.OKOG1.ES.53SDV110 | 2020-12-22 | 2020-12-30 | 2020-12-23 | 72FC | 4 | 31000136817 | 2020-12-04 | 2020-12-23 | 2020-12-22 | [5 empty] | ROTORK CP/S-035-100A/B SD VLV |  | ONTR | E | 11823946 | 921029 | CM |  | 0 | 2736 | 2736 | 1824
AFAINST | 22863524 | 2020-08-31 | A | 2020-08-31 | 2021-02-04 | XCNF XGI | TECO CNF ESTC NMAT PRC SETC | 53SDV120/DIS_ALM Fault | SD VLV, ESD SYS(COND TANK A),OKOG1 | NG.AFA.OKOG1.ES.53SDV120 | 2020-08-31 | 2021-02-04 | 2020-09-01 | 72FC | 6 | 31000136818 | 2020-08-09 | 2020-08-31 | 2020-08-31 | [5 empty] | ROTORK CP/S-035-100A/B SD VLV |  | ONTR |  | 11802294 | 900721 | CM |  | 0 | 1520 | 1520 | 1520
AFAINST | 22757198 | 2019-10-17 | A | 2019-10-17 | 2019-10-27 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | RESOLVE DIS_ALM/Solenoid valve Fail.on 5 | SD VLV, ESD SYS(COND TANK A),OKOG1 | NG.AFA.OKOG1.ES.53SDV120 | 2019-10-17 | 2019-10-27 | 2019-10-17 | 72FC | 6 | 31000136818 | 2019-05-03 | 2019-10-17 | 2019-10-17 | [5 empty] | ROTORK CP/S-035-100A/B SD VLV |  | ONTR | E | 11713583 | 820799 | CM |  | 0 | 1132.4 | 1132.4 | 1132.4
AFAINST | 22757199 | 2019-05-15 | A | 2019-05-15 | 2019-06-25 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | RESOLVE DIS_ALM/Solenoid valve Fail.on 5 | SD VLV, ESD SYS(COND TANK B),OKOG1 | NG.AFA.OKOG1.ES.53SDV220 | 2019-05-15 | 2019-06-25 | 2019-05-15 | 72FC | 5 | 31000136821 | 2019-05-03 | 2019-05-15 | 2019-05-15 | [5 empty] | ROTORK CP/S-035-100A/B SD VLV |  | ONTR | E | 11713580 | 820800 | CM |  | 0 | 1436.4 | 1436.4 | 1436.4
AFAINST | 22788177 | 2019-10-25 | A | 2019-10-25 | 2020-04-03 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | 56SDV210 Fail to open or close on demand | SD VLV, ESD SYS(F GAS COMP),OKOG1 | NG.AFA.OKOG1.ES.56SDV210 | 2019-10-25 | 2020-04-03 | 2019-10-25 | 72FC | 6 | 31000136855 | 2019-10-07 | 2019-10-25 | 2019-10-25 | [5 empty] | ORSENIGO FB2 SD VLV |  | ONTR | E | 11746150 | 848120 | CM |  | 0 | 684 | 684 | 684
AFAINST | 22680043 | 2018-08-25 | A | 2018-08-25 | 2018-08-29 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Rectify EPAF on 62SDV931(FIRE WATER DIST | SD VLV, ESD SYS(FIRE WATER DIST),OKOG1 | NG.AFA.OKOG1.ES.62SDV931 | 2018-08-25 | 2018-08-29 | 2018-08-26 | 72FC | 4 | 31000136889 | 2018-08-03 | 2018-08-25 | 2018-08-25 | [5 empty] | ROTORK CP/S-045-140A/B/FB SD VLV |  | ONTR | E | 11661236 | 768107 | CM |  | 0 | 836 | 836 | 836
AFAINST | 22871914 | 2020-10-05 | A | 2020-10-05 | 2020-10-13 | XCNF XGI | TECO CNF ESTC PRC SETC | Replace faulty regulator on 57SDV920 at | SD VLV, ESD SYS(GRF HP TO LP COND),OKOG1 | NG.AFA.OKOG1.ES.57SDV920 | 2020-10-05 | 2020-10-13 | 2020-10-05 | 72FC | 3 | 31000136873 | 2020-09-30 | 2020-10-05 | 2020-10-05 | [5 empty] | SHUTDOWN VALVE |  | ONTR | E | 11812273 | 909404 | CM |  | 0 | 342 | 1842 | 342
AFAINST | 22757195 | 2019-06-05 | A | 2019-06-05 | 2019-10-27 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | RESOLVE DIS_ALM/Solenoid valve Fail.on 5 | SD VLV, ESD SYS(H.P. DRUM 2),OKOG1 | NG.AFA.OKOG1.ES.52SDV240 | 2019-06-05 | 2019-10-27 | 2019-06-05 | 72FC | 6 | 31000136794 | 2019-05-03 | 2019-06-05 | 2019-06-05 | [5 empty] | ROTORK CP/S-045-140A/B SD VLV |  | ONTR | E | 11713587 | 820796 | CM |  | 0 | 600.4 | 600.4 | 600.4
AFAINST | 22706204 | 2018-11-23 | A | 2018-11-23 | 2019-05-17 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Service 52SDV241 stucked open at HP DRUM | SD VLV, ESD SYS(H.P. DRUM 2),OKOG1 | NG.AFA.OKOG1.ES.52SDV241 | 2018-11-23 | 2019-05-17 | 2018-11-23 | 72FC | 6 | 31000136795 | 2018-11-19 | 2018-11-23 | 2018-11-23 | [5 empty] | ROTORKCP/S065-280A/B+A90R/259MGV900SDV |  | SDTA | E | 11682089 | 788128 | CM |  | 0 | 1079.2 | 1079.2 | 1079.2
AFAINST | 22757196 | 2019-10-14 | A | 2019-10-14 | 2019-10-27 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | RESOLVE DIS_ALM/Solenoid valve Fail.on 5 | SD VLV, ESD SYS(L.P. DRUM 2),OKOG1 | NG.AFA.OKOG1.ES.52SDV340 | 2019-10-14 | 2019-10-27 | 2019-10-14 | 72FC | 6 | 31000136800 | 2019-05-03 | 2019-10-14 | 2019-10-14 | [5 empty] | ROTORK CP/S-055-200A/A SD VLV |  | ONTR | E | 11713629 | 820797 | CM |  | 0 | 760 | 760 | 760
AFAINST | 22875010 | 2020-11-10 | A | 2020-11-10 | 2020-12-13 | XCNF XGI | TECO CNF NMAT PRC SETC | Spurious MOD_BAD alarm on 32KSV400 | SD VLV, ESD SYS(TWISTER PACKAGE),OKOG1 | NG.AFA.OKOG1.ES.32KSV400 | 2020-11-10 | 2020-12-13 | 2020-11-11 | 72FC | 5 | 31000136655 | 2020-10-19 | 2020-11-10 | 2020-11-10 | [5 empty] | MOKVELD RZD-X SD VLV |  | ONTR |  | 11815363 | 912257 | CM |  | 0 | 760 | 760 | 760
AFAINST | 22715177 | 2019-03-04 | A | 2019-03-04 | 2019-06-25 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Rectify 32KSV300/MOD_BAD on Tube 3 TWSIT | SD VLV, ESD SYS(TWISTER PACKAGE),OKOG1 | NG.AFA.OKOG1.ES.32KSV300 | 2019-03-04 | 2019-06-25 | 2019-03-04 | 72FC | 6 | 31000136653 | 2018-12-29 | 2019-03-04 | 2019-03-04 | [5 empty] | MOKVELD RZD-X SD VLV |  | ONTR | E | 11689457 | 795173 | CM |  | 0 | 752.4 | 752.4 | 752.4
AFAINST | 22715178 | 2019-03-08 | A | 2019-03-08 | 2019-06-25 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Rectify 32KSV400/MOD_BAD on Tube 4 TWSIT | SD VLV, ESD SYS(TWISTER PACKAGE),OKOG1 | NG.AFA.OKOG1.ES.32KSV400 | 2019-03-08 | 2019-06-25 | 2019-03-08 | 72FC | 6 | 31000136655 | 2018-12-29 | 2019-03-08 | 2019-03-08 | [5 empty] | MOKVELD RZD-X SD VLV |  | ONTR | E | 11689459 | 795174 | CM |  | 0 | 752.4 | 752.4 | 752.4
AFAINST | 22849585 | 2020-06-15 | A | 2020-06-15 | 2020-12-04 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Tube 6 32KSV601 module suspected faulty | SD VLV, ESD SYS(TWISTER PACKAGE),OKOG1 | NG.AFA.OKOG1.ES.32KSV601 | 2020-06-15 | 2020-12-04 | 2020-06-15 | 72FC | 6 | 31000136660 | 2020-06-09 | 2020-06-15 | 2020-06-15 | [5 empty] | ORSENIGO FB BALL VALVE SD VLV |  | ONTR |  | 11791395 | 890213 | CM |  | 0 | 608 | 1368 | 608
AFAINST | 22711258 | 2019-06-03 | A | 2019-06-03 | 2019-06-06 | XCNF MANX XGI | CLSD CNF ESTC GMPS PRC SETC | Rectify 10KSV900 failed on demand at RM | SD VLV, ESD SYS(WELL F10F14-22),OKOG1 | NG.AFA.OKOG1.ES.10KSV900 | 2019-06-03 | 2019-06-06 | 2019-06-03 | 72FC | 6 |  | 2018-12-09 | 2019-06-03 | 2019-06-03 | [7 empty] | ONTR | E | 11686154 | 791989 | CM |  | 0 | 5417.84 | 5417.84 | 5227.71
AFAINST | 22787893 | 2019-12-22 | A | 2019-12-22 | 2020-04-03 | XCNF XGI | CLSD CNF NMAT PRC SETC | Rectify 51SDV120 fails to open/close on | SD VLV, ESD SYS(XHP DRUM 1),OKOG1 | NG.AFA.OKOG1.ES.51SDV120 | 2019-12-22 | 2020-04-03 | 2019-12-22 | 72FC | 6 | 31000136746 | 2019-10-06 | 2019-12-22 | 2019-12-22 | [5 empty] | ROTORKCP/S065-280A/B+A90R/259MGV900SDV |  | ONTR | E | 11746148 | 848016 | CM |  | 0 | 608 | 608 | 608
AFAINST | 22804421 | 2019-12-23 | A | 2019-12-23 | 2020-01-08 | XCNF XGI | CLSD CNF PRT NMAT PRC SETC | RECTIFY FAULT ON 52 SDV-121 not closing | SD VLV, ESD SYS(XHP DRUM 2),OKOG1 | NG.AFA.OKOG1.ES.52SDV121 | 2019-12-23 | 2020-01-08 | 2019-12-23 | 72FC | 4 | 31000136790 | 2019-12-15 | 2019-12-23 | 2019-12-23 | [5 empty] | ROTORKCP/S-045-180/C-A90R/259MGV900SDV |  | ONTR | E | 11759025 | 860161 | CM |  | 0 | 912 | 912 | 912
AFAINST | 22788176 | 2019-10-25 | A | 2019-10-25 | 2020-04-03 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | 52SDV121 Fail to open or close on demand | SD VLV, ESD SYS(XHP DRUM 2),OKOG1 | NG.AFA.OKOG1.ES.52SDV121 | 2019-10-25 | 2020-04-03 | 2019-10-25 | 72FC | 6 | 31000136790 | 2019-10-07 | 2019-10-25 | 2019-10-25 | [5 empty] | ROTORKCP/S-045-180/C-A90R/259MGV900SDV |  | ONTR | E | 11746151 | 848119 | CM |  | 0 | 646 | 646 | 646
AFAINST | 22681697 | 2018-08-13 | A | 2018-08-13 | 2018-08-15 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Rectify Instrument air leak on 57SDV908 | SDV, MAIN INLET 1, GAS SEP SYS, AFAM GRF | NG.AFA.AFAG2.ES.57SDV908 | 2018-08-13 | 2018-08-15 | 2018-08-13 | 72FC | 2 |  | 2018-08-09 | 2018-08-13 | 2018-08-13 | [7 empty] | SDTA |  | 11662672 | 769199 | CM |  | 0 | 456 | 456 | 456
AFAINST | 22879746 | 2020-11-26 | A | 2020-11-27 | 2021-10-22 | XCNF XGI | TECO CNF ESTC NMAT PRC SETC | Stop air leaks on Volme booster on 53SDV | SHUT DOWN VALVE COND TRANS SYS, OKOG1 | NG.AFA.OKOG1.ES.53SDV305 | 2020-11-26 | 2021-10-22 | 2020-11-27 | 72FC | 7 |  | 2020-11-12 | 2020-11-27 | 2020-11-26 | [7 empty] | ONTR | E | 11817087 | 916223 | CM |  | 0 | 1064 | 1064 | 304
AFAINST | 22757194 | 2019-10-26 | A | 2019-10-26 | 2019-10-27 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | RESOLVE DIS_ALM/Solenoid valve Fail.on 5 | SHUT DOWN VALVE COND TRANS SYS, OKOG1 | NG.AFA.OKOG1.ES.53SDV305 | 2019-10-26 | 2019-10-27 | 2019-10-26 | 72FC | 6 |  | 2019-05-03 | 2019-10-26 | 2019-10-26 | [7 empty] | ONTR | E | 11713541 | 820795 | CM |  | 0 | 836 | 1064 | 836
AFAINST | 22700168 | 2019-07-12 | B | 2019-07-13 | 2019-07-31 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Repair Leaking actuator on 10SDV120 at W | SHUTDOWN VALVE,SWING WELL PIG RECV,OKOG1 | NG.AFA.OKOG1.ES.10SDV120 | 2019-07-12 | 2019-04-23 | 2019-07-14 | 72FC | 6 | 31000175281 | 2018-10-26 | 2019-07-13 | 2019-07-12 | [5 empty] | SHUTDOWN VALVE,SWING WELL PIG RECEIVER |  | ONTR | E | 11677260 | 783719 | CM |  | 0 | 2432 | 2432 | 2432
AFAINST | 22632034 | 2018-03-05 | B | 2018-03-05 | 2018-03-17 | XCNF XGI | TECO CNF CSER NMAT PRC SETC | Stop leak on 10SDV120 @ W/27T line | SHUTDOWN VALVE,SWING WELL PIG RECV,OKOG1 | NG.AFA.OKOG1.ES.10SDV120 | 2018-03-05 | 2018-03-17 | 2018-03-06 | 72FC | 5 | 31000175281 | 2018-01-21 | 2018-03-05 | 2018-03-05 | [5 empty] | SHUTDOWN VALVE,SWING WELL PIG RECEIVER |  | SDTA | E | 11618584 | 729995 | CM |  | 0 | 0 | 0 | 0
AFAINST | 22837709 | 2020-07-14 | A | 2020-07-14 | 2020-10-09 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Discrepancy alarm on XXHP 52SDV511 | SHUTDOWN VALVE1,XXHP SEPARATOR,OKOG1 | NG.AFA.OKOG1.ES.52SDV511 | 2020-07-14 | 2020-10-09 | 2020-07-15 | 72FC | 6 | 31000180777 | 2020-04-18 | 2020-07-14 | 2020-07-14 | [5 empty] | CAMERON LEEDEN TYPE-BALL/66616SRC8 VALVE |  | ONTR |  | 11782248 | 882485 | CM |  | 0 | 1520 | 1000 | 1520
AFAINST | 22797136 | 2019-12-31 | A | 2019-12-31 | 2020-01-03 | XCNF XGI | CLSD CNF NMAT PRC SETC | Rectify 51SDV140 leaks from Nipple | SHUTDOWN VALVE2,XXHP SEPARATOR,OKOG1 | NG.AFA.OKOG1.ES.51SDV140 | 2019-12-31 | 2020-01-03 | 2019-12-31 | 72FC | 5 | 31000180778 | 2019-11-14 | 2019-12-31 | 2019-12-31 | [5 empty] | DELLA FOGLIA/BIFFI,TN/0.9C-0700-385,SDV2 |  | ONTR |  | 11753152 | 854669 | CM |  | 0 | 684 | 684 | 684
AFAINST | 22749826 | 2019-04-13 | A | 2019-04-13 | 2019-05-25 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Carryout Integrity chks on 45SDV001 GRF | SHUTDOWN VLV,INLET MANIFOLD SYS,AFAM GRF | NG.AFA.AFAG2.ES.45SDV001 | 2019-04-13 | 2019-05-25 | 2019-04-13 | 72FC | 5 | 31000101144 | 2019-03-31 | 2019-04-13 | 2019-04-13 | [5 empty] | VALVITALIA,LPS-13-640-CM30-FC,6"X300#SDV |  | ONTR | E | 11707355 | 815164 | CM |  | 0 | 836 | 836 | 836
AFAINST | 22756582 | 2019-05-15 | A | 2019-05-15 | 2019-06-23 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Resolve DIS_ALM/Solenoid valve Fail on 5 | SHUTDWN VLV301, CONDENSATE PPKG-5302, ES | NG.AFA.OKOG1.ES.53SDV301 | 2019-05-15 | 2019-06-23 | 2019-05-15 | 72FC | 5 | 31000190981 | 2019-04-30 | 2019-05-15 | 2019-05-15 | [5 empty] | TK MODEL BS6RA74333 SHUTDOWN VALVE |  | ONTR | E | 11713131 | 820572 | CM |  | 0 | 668.8 | 668.8 | 668.8
AFAINST | 22748878 | 2019-08-26 | B | 2019-08-26 | 2019-09-20 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Rectify 53SDV301 Solenoid valve failed | SOLENOID VLV301, CONDENSATE PPKG5302, ES | NG.AFA.OKOG1.ES.53EV301 | 2019-08-26 | 2019-09-20 | 2019-08-28 | 72FC | 6 |  | 2019-03-25 | 2019-08-26 | 2019-08-26 | [7 empty] | ONTR | E | 11706265 | 814332 | CM |  | 0 | 988 | 988 | 912
AFAINST | 22629387 | 2018-07-07 | A | 2018-07-07 | 2018-07-08 | XCNF MANX XGI | CLSD CNF PRC SETC | Rectify Failure of 32KSV600 Tube 6 Inlet | SOV, 32KSV600 SD VLV, ESD SYS, OKOG1 | NG.AFA.OKOG1.ES.32EV600 | 2018-07-07 | 2018-07-08 | 2018-07-07 | 72FC | 6 |  | 2018-01-10 | 2018-07-07 | 2018-07-07 | [7 empty] | ONTR | E | 11616357 | 727926 | CM |  | 0 | 20864.02 | 0 | 1444
AFAINST | 22656564 | 2018-05-02 | A | 2018-05-02 | 2018-05-23 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Rectify 52SDV400 failure to open at AP D | SOV, 52SDV400 SD VLV, ESD SYS, OKOG1 | NG.AFA.OKOG1.ES.52EV400 | 2018-05-02 | 2018-05-23 | 2018-05-02 | 72FC | 4 |  | 2018-04-28 | 2018-05-02 | 2018-05-02 | [7 empty] | ONTR | E | 11639548 | 749143 | CM |  | 0 | 912 | 912 | 836
AFAINST | 22757192 | 2019-05-14 | A | 2019-05-14 | 2019-06-25 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | RESOLVE DIS_ALM/Solenoid valve Fail.on 5 | SOV, 53SDV110 SD VLV, ESD SYS, OKOG1 | NG.AFA.OKOG1.ES.53EV110 | 2019-05-14 | 2019-06-25 | 2019-05-14 | 72FC | 5 |  | 2019-05-03 | 2019-05-14 | 2019-05-14 | [7 empty] | ONTR | E | 11713577 | 820794 | CM |  | 0 | 1018.4 | 1018.4 | 1018.4
AFAINST | 22753144 | 2019-04-24 | A | 2019-04-24 | 2019-05-13 | XCNF MANX XGI | CLSD CNF ESTC PRC SETC | Stop leak on W24 SDV 09SDV110 IA Regulat | TANGO STRING FLOWLINE, WELL 24, OKOLOMA | NG.AFA.OKOG1.FL.AFAM WELL 24T | 2019-04-24 | 2019-05-13 | 2019-04-24 | 72FC | 4 |  | 2019-04-15 | 2019-04-24 | 2019-04-24 | [7 empty] | ONTR | E | 11710298 | 817621 | CM |  | 0 | 979.69 | 979.69 | 608
AFAINST | 22779120 | 2019-09-03 | A | 2019-09-03 | 2019-09-19 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Resolve Failure of 52BDV500, XXHP Separa | VLV PSTN TRANSMITR2,XXHP SEPARATOR,OKOG1 | NG.OKOG1.V-5205-52GIT500 | 2019-09-03 | 2019-09-19 | 2019-09-04 | 72FC | 4 |  | 2019-08-25 | 2019-09-03 | 2019-09-03 | [7 empty] | ONTR | E | 11736261 | 840453 | CM |  | 0 | 744.8 | 744.8 | 744.8