## Air Compressor
[5 empty] | 2018 | 2019 | 2020
|  |  |  | CM Costs | 16063.51 | 16059.06 | 10028.54
|  |  |  | CM count | 10 | 3 | 13
Failure Modes
Components | Failure Mode | Frequency
Compressor | Scroll damage | 7
Electric motor | Motor bearing & overload fault | 5
| Motor oil ingress failure | 2
Lubrication system | Oil leaks | 1
Miscellaneous | Dryer system failure (air leaks, clogged filter) | 3
| Air reciever failures (auto drain, air leaks) | 5
| Faulty control components | 2
| loss of power supply | 1
| Compressor- related failures | 7 | 26.92%
| Electric motor - related failures | 7 | 26.92%
| Lube system- related failures | 1
| Miscellaneous failures | 11

## Notifications
Required End | Priority | Notification | Breakdown | Description | Functional Location | Notification date | System status | User Status | Created On | Equipment | Maintenance Plan | Order | Priority type | Priority text | SCE Group | ABC indicator | Catalog profile | FunctLocDescrip. | Object Description | Completion by date | Master insp.charac. | Notification type
20201101 | 5 | 11808048 | X | FAULTY ELECT MOTOR KM-6808 | NG.OKOG1.K-6808-KM6808 | 2020-09-06 | NOCO ORAS | CLSD | 2020-09-06 | 31000175302 |  | 22868489 | CM | Complete by 8 Weeks | IC003 | A | CP_ELE301 | MOT,INSTR AIR COMPR PKG B,OKOG1 | ATLAS COPCO,YXLA200L2,ELECTRIC MOTOR | 2020-10-31 |  | Z1
20200907 | 5 | 11797821 | X | K6808 trips on high element temperature | NG.OKOG1.K-6808-K6808LOD | 2020-07-13 | NOCO ORAS | CLSD | 2020-07-13 | 31000175301 |  | 22857360 | CM | Complete by 8 Weeks |  | A | CP_ROT101 | INSTR AIR COMPR B,I/AIR SYS,OKOG1 | ATLAS COPCO :GA37+,INSTRMNT AIR COMPRESR | 2020-07-23 |  | Z1
20191216 | 5 | 11749327 |  | K-6808 running with low efficiency | NG.OKOG1.K-6808-K6808LOD | 2019-10-21 | NOCO ORAS | CLSD | 2019-10-21 | 31000175301 |  | 22792128 | CM | Complete by 8 Weeks |  | A | CP_ROT101 | INSTR AIR COMPR B,I/AIR SYS,OKOG1 | ATLAS COPCO :GA37+,INSTRMNT AIR COMPRESR | 2019-11-26 |  | Z1
20201224 | 5 | 11817452 | X | FAULTY CONTROL COMPONENTS ON K-6808 | NG.OKOG1.K-6808-K6808LOD | 2020-10-29 | NOCO ORAS | CLSD | 2020-10-29 | 31000175301 |  | 22879718 | CM | Complete by 8 Weeks |  | A | CP_ROT101 | INSTR AIR COMPR B,I/AIR SYS,OKOG1 | ATLAS COPCO :GA37+,INSTRMNT AIR COMPRESR | 2020-12-27 |  | Z1
20180408 | 5 | 11623690 | X | FAULTY ATLAS-COPCO AIR COMPRESSOR K-6808 | NG.OKOG1.K-6808-K6808LOD | 2018-02-11 | NOCO ORAS | CLSD | 2018-02-11 | 31000175301 |  | 22639008 | CM | Complete by 8 Weeks |  | A | CP_ROT101 | INSTR AIR COMPR B,I/AIR SYS,OKOG1 | ATLAS COPCO :GA37+,INSTRMNT AIR COMPRESR | 2019-01-02 |  | Z1
20201130 | 5 | 11813185 |  | K6808 compressor stopped working | NG.OKOG1.K-6808-KM6808 | 2020-10-05 | NOCO ORAS | CLSD | 2020-10-05 | 31000175302 |  | 22872634 | CM | Complete by 8 Weeks | IC003 | A | CP_ELE301 | MOT,INSTR AIR COMPR PKG B,OKOG1 | ATLAS COPCO,YXLA200L2,ELECTRIC MOTOR | 2020-11-30 |  | Z1
20190722 | 6 | 11694780 | X | Oil leak on air compressor K-6808 motor | NG.OKOG1.K-6808-KM6808 | 2019-01-23 | NOCO ORAS | CLSD | 2019-01-23 | 31000175302 |  | 22737861 | CM | Complete by 6 Months | IC003 | A | CP_ELE301 | MOT,INSTR AIR COMPR PKG B,OKOG1 | ATLAS COPCO,YXLA200L2,ELECTRIC MOTOR | 2019-09-20 |  | Z1
20181210 | 5 | 11675580 | X | Unusual noise on K-6809 Air compressor | NG.OKOG1.K-6809-KM6809 | 2018-10-15 | NOCO ORAS | CLSD | 2018-10-15 | 31000175306 |  | 22697807 | CM | Complete by 8 Weeks | IC003 | A | CP_ELE301 | MOT,INSTR AIR COMPR PKG C,OKOG1 | ATLAS COPCO,YXLA200L2,ELECTRIC MOTOR | 2019-10-19 |  | Z1
20201010 | 6 | 11782547 | X | High noise on KM-6809 | NG.OKOG1.K-6809-KM6809 | 2020-04-13 | NOCO ORAS | CLSD | 2020-04-13 | 31000175306 |  | 22836813 | CM | Complete by 6 Months | IC003 | A | CP_ELE301 | MOT,INSTR AIR COMPR PKG C,OKOG1 | ATLAS COPCO,YXLA200L2,ELECTRIC MOTOR | 2020-10-18 |  | Z1
20180824 | 4 | 11660291 | X | AIR COMPRESSOR K-6806 AUTO DRAIN LEAKING | NG.OKOG1.K-6806-K-6806LOD | 2018-07-27 | NOCO ORAS | CLSD | 2018-07-27 | 31000167011 |  | 22678377 | CM | Complete by 4 Weeks |  | B | CP_ROT102 | COMPRESSOR, INST AIR COMP K-6806, OKOG1 | ATLAS COPCO MODEL GA37P AIR COMPRESSOR | 2018-07-31 |  | Z1
20201014 | 6 | 11783147 |  | Air leaks from Comp. K6806 Auto-drain | NG.OKOG1.K-6806-K-6806LOD | 2020-04-17 | NOCO ORAS | CLSD | 2020-04-17 | 31000167011 |  | 22838114 | CM | Complete by 6 Months |  | B | CP_ROT102 | COMPRESSOR, INST AIR COMP K-6806, OKOG1 | ATLAS COPCO MODEL GA37P AIR COMPRESSOR | 2020-06-10 |  | Z1
20210621 | 6 | 11828111 | X | Air compr K-6807 trip on motor overload | NG.OKOG1.K-6807-K6807LOD | 2020-12-23 | NOPR ORAS | APPR | 2020-12-23 | 31000175297 |  | 22889581 | CM | Complete by 6 Months |  | A | CP_ROT101 | INSTR AIR COMPR A,I/AIR SYS,OKOG1 | ATLAS COPCO,GA37+,INSTRMNT AIR COMPRESR |  |  | Z1
20190428 | 6 | 11678273 |  | No auto drain on A/Copco air receivers | NG.AFA.OKOG1.IA | 2018-10-30 | NOCO ORAS | CLSD | 2018-10-30 |  |  | 22701565 | CM | Complete by 6 Months | SD009 | B | NO_MAINT1 | INST AIR SYS, OKOG1 |  | 2019-05-01 |  | Z1
20180927 | 4 | 11666560 |  | K6809 trips incessantly | NG.AFA.OKOG1.IA.K-6809 | 2018-08-30 | NOCO ORAS | CLSD | 2018-08-30 |  |  | 22687238 | CM | Complete by 4 Weeks |  | B | CP_ROT101 | ROTARY AIR COMPR A,I/AIR SYS,OKOG1 |  | 2018-09-17 |  | Z1
20210316 | 6 | 11809951 | X | TROUBLESHOOT FAULT ON K-6809 | NG.AFA.OKOG1.IA.K-6809 | 2020-09-17 | NOPR ORAS | APPR | 2020-09-17 |  |  | 22869977 | CM | Complete by 6 Months |  | B | CP_ROT101 | ROTARY AIR COMPR A,I/AIR SYS,OKOG1 |  |  |  | Z1
20181212 | 3 | 11684019 | X | No power to K6807 inst air comp. | NG.OKOG1.A-6807-CP6807 | 2018-11-28 | NOCO ORAS | CLSD | 2018-11-28 | 31000175294 |  | 22709052 | CM | Complete by 2 Weeks |  | C | CP_ELE302 | CTRL PNL,INSTR AIR COMPR PKG A | ATLAS COPCO,GA37+,CNTRL PNL I/AIR PKG A | 2018-12-10 |  | Z1
20180820 | 3 | 11662121 | X | Instr. air comp. K6807 faulty | NG.OKOG1.A-6807-CP6807 | 2018-08-05 | NOCO ORAS | CLSD | 2018-08-06 | 31000175294 |  | 22680778 | CM | Complete by 2 Weeks |  | C | CP_ELE302 | CTRL PNL,INSTR AIR COMPR PKG A | ATLAS COPCO,GA37+,CNTRL PNL I/AIR PKG A | 2018-08-14 |  | Z1
20180820 | 3 | 11662122 | X | Instr. air comp. K6809 faulty | NG.OKOG1.A-6809-CP6809 | 2018-08-06 | NOCO ORAS | CLSD | 2018-08-06 | 31000175296 |  | 22680779 | CM | Complete by 2 Weeks |  | C | CP_ELE302 | CTRL PNL,INSTR AIR COMPR PKG C | ATLAS COPCO,GA37+,CNTRL PNL I/AIR PKG C | 2018-08-14 |  | Z1
20200311 | 4 | 11771581 | X | Air compressor K-6809 cooler fan fault | NG.OKOG1.A-6809-CP6809 | 2020-02-12 | NOCO ORAS | CLSD | 2020-02-12 | 31000175296 |  | 22822135 | CM | Complete by 4 Weeks |  | C | CP_ELE302 | CTRL PNL,INSTR AIR COMPR PKG C | ATLAS COPCO,GA37+,CNTRL PNL I/AIR PKG C | 2020-03-07 |  | Z1
20201229 | 4 | 11823689 |  | Atlas Copco K6807 tripped couldn't reset | NG.OKOG1.K-6807-KM6807 | 2020-12-01 | NOCO ORAS | CLSD | 2020-12-01 | 31000175298 |  | 22884944 | CM | Complete by 4 Weeks | IC003 | A | CP_ELE301 | MOT,INSTR AIR COMPR PKG A,OKOG1 | ATLAS COPCO,YXLA200L2,ELECTRIC MOTOR | 2021-01-01 |  | Z1
20180927 | 4 | 11666559 | X | K6807 trips incessantly | NG.AFA.OKOG1.IA.K-6807 | 2018-08-30 | NOCO ORAS | CLSD | 2018-08-30 |  |  | 22687237 | CM | Complete by 4 Weeks |  | B | CP_ROT101 | ROTARY AIR COMPR A,I/AIR SYS,OKOG1 |  | 2018-09-04 |  | Z1
20210122 | 5 | 11823221 |  | Air leaks on dryer B filter D-6860 | NG.AFA.OKOG1.IA.S-6807 | 2020-11-27 | NOPR ORAS | APPR | 2020-11-27 | 31000175299 |  | 22883467 | CM | Complete by 8 Weeks |  | B | CP_STA506 | AIR FILTER,INSTR AIR COMPR PKG A,OKOG1 | ATLAS COPCO,AIR FILTER |  |  | Z1
20210410 | 6 | 11814473 |  | Air receiver leaking from side plug | NG.AFA.OKOG1.IA.V-6808 | 2020-10-12 | NOCO ORAS | CLSD | 2020-10-12 | 31000175304 |  | 22873958 | CM | Complete by 6 Months | SD009 | A | CP_STA506 | AIR RECVR,INSTR AIR COMPR PKG B,OKOG1 | ATLAS COPCO,1622310099,AIR RECEIVER | 2020-11-01 |  | Z1
20191216 | 5 | 11749316 | X | K6805 running with unusual noise | NG.OKOG1.K-6805-EM-6805 | 2019-10-21 | NOPR ORAS | APPR | 2019-10-21 | 31000167008 |  | 22791589 | CM | Complete by 8 Weeks | IC003 | A | CP_ELE301 | MOTOR, INST AIR COMP K-6805, OKOG1 | SIEMENS MOD ILA5209-2AA90-Z100 MOTOR |  |  | Z1
20180408 | 5 | 11623689 | X | FAULTY ATLAS-COPCO AIR COMPRESSOR K-6809 | NG.OKOG1.K-6809-K6809LOD | 2018-02-11 | NOCO ORAS | CLSD | 2018-02-11 | 31000175305 |  | 22639009 | CM | Complete by 8 Weeks |  | A | CP_ROT101 | INSTR AIR COMPR C,I/AIR SYS,OKOG1 | ATLAS COPCO,GA37+,INSTRMNT AIR COMPRESR | 2018-06-08 |  | Z1
20201023 | 5 | 11806207 |  | Instr. Air Comp. K6808 faulty | NG.OKOG1.A-6808-CP6808 | 2020-08-28 | NOCO ORAS | CLSD | 2020-08-28 | 31000175295 |  | 22868175 | CM | Complete by 8 Weeks |  | C | CP_ELE302 | CTRL PNL,INSTR AIR COMPR PKG B | ATLAS COPCO,GA37+,CNTRL PNL I/AIR PKG B | 2020-09-25 |  | Z1

## WO
Main work center | Order | Basic start date | ABC indicator | Scheduled finish | Latest Allowed Finish Date | User Status | System status | Description | FunctLocDescrip. | Functional Location | Scheduled start | Original Latest Allowed Finish Date | Actual Finish Date | Order Type | Priority | Equipment | Created on | Basic finish date | Actual start date | Group | Group Counter | Maintenance item | Maintenance Plan | Cost Center | Object Description | Assembly desc. | Execution Condition | Long text exists | Notification | Object list | Priority type | PO Number | System Condition | Total planned costs | Estimated costs | Total actual costs
AFAINST | 22680778 | 2018-08-14 | C | 2018-08-14 | 2018-08-20 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Troubleshoot faulty Instr. air comp. K68 | CTRL PNL,INSTR AIR COMPR PKG A | NG.OKOG1.A-6807-CP6807 | 2018-08-14 | 2018-08-20 | 2018-08-14 | 72FC | 3 | 31000175294 | 2018-08-06 | 2018-08-14 | 2018-08-14 | [5 empty] | ATLAS COPCO,GA37+,CNTRL PNL I/AIR PKG A |  | ONTR | E | 11662121 | 768422 | CM |  | 0 | 532 | 228 | 532
AFAELEC | 22868175 | 2020-09-10 | C | 2020-09-10 | 2020-10-23 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Troubleshoot Instr. Air Comp. K-6808 fau | CTRL PNL,INSTR AIR COMPR PKG B | NG.OKOG1.A-6808-CP6808 | 2020-09-10 | 2020-10-23 | 2020-09-10 | 72FC | 5 | 31000175295 | 2020-09-06 | 2020-09-10 | 2020-09-10 | [5 empty] | ATLAS COPCO,GA37+,CNTRL PNL I/AIR PKG B |  | ONTR | E | 11806207 | 905539 | CM |  | 0 | 1094.4 | 1094.4 | 1102
AFAELEC | 22680779 | 2018-08-14 | C | 2018-08-14 | 2018-08-20 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Faulty Instr. air comp. K6809 | CTRL PNL,INSTR AIR COMPR PKG C | NG.OKOG1.A-6809-CP6809 | 2018-08-14 | 2018-08-20 | 2018-08-14 | 72FC | 3 | 31000175296 | 2018-08-06 | 2018-08-14 | 2018-08-14 | [5 empty] | ATLAS COPCO,GA37+,CNTRL PNL I/AIR PKG C |  | ONTR |  | 11662122 | 768423 | CM |  | 0 | 228 | 228 | 228
AFAMECH | 22857360 | 2020-07-20 | A | 2020-07-21 | 2020-09-07 | XCNF XGI | CLSD CNF NMAT PRC SETC | Restoration of Atlas Copco K-6808 | INSTR AIR COMPR B,I/AIR SYS,OKOG1 | NG.OKOG1.K-6808-K6808LOD | 2020-07-20 | 2020-09-07 | 2020-07-21 | 72FC | 5 | 31000175301 | 2020-07-15 | 2020-07-21 | 2020-07-20 | [5 empty] | ATLAS COPCO :GA37+,INSTRMNT AIR COMPRESR |  | ONTR |  | 11797821 | 896662 | CM |  | 0 | 1246.4 | 1246.4 | 1246.4
AFAMECH | 22792128 | 2019-11-26 | A | 2019-11-26 | 2019-12-16 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | K-6808 running with low efficiency | INSTR AIR COMPR B,I/AIR SYS,OKOG1 | NG.OKOG1.K-6808-K6808LOD | 2019-11-26 | 2019-12-16 | 2019-11-26 | 72FC | 5 | 31000175301 | 2019-10-23 | 2019-11-26 | 2019-11-26 | [5 empty] | ATLAS COPCO :GA37+,INSTRMNT AIR COMPRESR |  | ONTR |  | 11749327 | 851118 | CM |  | 0 | 608 | 608 | 608
AFAMECH | 22639008 | 2018-12-24 | A | 2018-12-31 | 2018-12-31 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | REPAIR FAULTY ATLAS-COPCO AIR COMPRESSOR | INSTR AIR COMPR B,I/AIR SYS,OKOG1 | NG.OKOG1.K-6808-K6808LOD | 2018-12-24 | 2018-04-08 | 2018-12-31 | 72FC | 5 | 31000175301 | 2018-02-15 | 2018-12-31 | 2018-06-06 | [5 empty] | ATLAS COPCO :GA37+,INSTRMNT AIR COMPRESR |  | ONTR | E | 11623690 | 735316 | CM |  | 0 | 114 | 3990 | 3997.6
AFAMECH | 22639009 | 2018-06-06 | A | 2018-06-08 | 2018-06-30 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | REPAIR FAULTY ATLAS-COPCO AIR COMPR K-68 | INSTR AIR COMPR C,I/AIR SYS,OKOG1 | NG.OKOG1.K-6809-K6809LOD | 2018-06-06 | 2018-04-08 | 2018-06-06 | 72FC | 5 | 31000175305 | 2018-02-15 | 2018-06-08 | 2018-06-06 | [5 empty] | ATLAS COPCO,GA37+,INSTRMNT AIR COMPRESR |  | ONTR | E | 11623689 | 735317 | CM |  | 0 | 3891.2 | 3891.2 | 3868.4
AFAMECH | 22518687 | 2018-02-15 | A | 2018-02-16 | 2018-01-19 | XCNF MANX XGI | TECO CNF ESTC CSER GMPS PRC SETC | Restoration of Atlas Copco K6809 | INSTR AIR COMPR C,I/AIR SYS,OKOG1 | NG.OKOG1.K-6809-K6809LOD | 2018-02-15 | 2018-01-19 | 2018-02-10 | 72FC | 7 | 31000175305 | 2017-01-26 | 2018-02-16 | 2018-02-10 | [5 empty] | ATLAS COPCO,GA37+,INSTRMNT AIR COMPRESR |  | ONTR |  | 11533471 | 644362 | CM |  | 0 | 2911.8 | 4462.2 | 2086.09
AFAELEC | 22883550 | 2020-11-30 | A | 2020-12-11 |  | APPR | REL GMPS NMAT PRC SETC | REPAIR OF AIR COMPR K6808 @ OKGP | MOT,INSTR AIR COMPR PKG B,OKOG1 | NG.OKOG1.K-6808-KM6808 | 2020-12-11 |  |  | 72RE | 2 | 31000175302 | 2020-11-30 | 2020-12-30 | [6 empty] | ATLAS COPCO,YXLA200L2,ELECTRIC MOTOR |  |  |  |  | 0 | GM |  |  | 4929.18 | 3456.21 | 1472.97
AFAELEC | 22775541 | 2019-08-11 | A | 2019-08-11 |  | APPR | REL ESTC GMPS NMAT PRC SETC | INSTALLATION & TERMINATION OF K-6808/9 T | MOT,INSTR AIR COMPR PKG B,OKOG1 | NG.OKOG1.K-6808-KM6808 | 2019-08-11 |  |  | 72RE | 3 |  | 2019-08-06 | 2019-11-04 | [9 empty] | E |  | 0 | GM |  |  | 11722.26 | 11722.26 | 11722.26
AFAELEC | 22836813 | 2020-10-08 | A | 2020-10-10 | 2020-10-10 | XCNF XGI | TECO CNF ESTC GMPS NMAT PRC SETC | Rectify High noise on KM-6809 | MOT,INSTR AIR COMPR PKG C,OKOG1 | NG.OKOG1.K-6809-KM6809 | 2020-10-08 | 2020-10-10 | 2020-10-08 | 72FC | 6 | 31000175306 | 2020-04-14 | 2020-10-10 | 2020-10-08 | [5 empty] | ATLAS COPCO,YXLA200L2,ELECTRIC MOTOR |  | ONTR |  | 11782547 | 881773 | CM |  | 0 | 2023.05 | 1580.8 | 1871.05
AFAELEC | 22697807 | 2019-10-16 | A | 2019-10-16 | 2019-12-31 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Unusual noise on K-6809 Air compressor | MOT,INSTR AIR COMPR PKG C,OKOG1 | NG.OKOG1.K-6809-KM6809 | 2019-10-16 | 2018-12-10 | 2019-10-16 | 72FC | 5 | 31000175306 | 2018-10-16 | 2019-10-16 | 2019-10-16 | [5 empty] | ATLAS COPCO,YXLA200L2,ELECTRIC MOTOR |  | ONTR |  | 11675580 | 781359 | CM |  | 0 | 616 | 608 | 616
AFAINST | 22874436 | 2020-10-29 | A | 2020-10-30 | 2020-12-08 | XCNF XGI | TECO CNF ESTC NMAT PRC SETC | Air reciever 68 LCV 202 faulty | LEVEL CNTRL VALVE202,AIR RECE 6801,OKOG1 | NG.OKOG1.V-6802-68LCV202 | 2020-10-29 | 2020-12-08 | 2020-10-31 | 72FC | 5 |  | 2020-10-15 | 2020-10-30 | 2020-10-29 | [7 empty] | ONTR | E | 11814612 | 911635 | CM |  | 0 | 798 | 798 | 798
AFAINST | 22701565 | 2019-04-22 | B | 2019-04-28 | 2019-04-28 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Installation of auto drain on A/Copco ai | INST AIR SYS, OKOG1 | NG.AFA.OKOG1.IA | 2019-04-22 | 2019-04-28 | 2019-04-28 | 72FC | 6 |  | 2018-10-31 | 2019-04-28 | 2019-04-22 | [7 empty] | ONTR | E | 11678273 | 784461 | CM |  | 0 | 1884.8 | 1884.8 | 2188.8
AFAMECH | 22873958 | 2020-10-31 | A | 2020-10-31 | 2021-04-10 | XCNF XGI | TECO CNF ESTC NMAT PRC SETC | Air receiver leaking from side plug | AIR RECVR,INSTR AIR COMPR PKG B,OKOG1 | NG.AFA.OKOG1.IA.V-6808 | 2020-10-31 | 2021-04-10 | 2020-10-31 | 72FC | 6 | 31000175304 | 2020-10-13 | 2020-10-31 | 2020-10-31 | [5 empty] | ATLAS COPCO,1622310099,AIR RECEIVER |  | ONTR |  | 11814473 | 911371 | CM |  | 0 | 152 | 152 | 152
AFAINST | 22838114 | 2020-06-09 | B | 2020-06-09 | 2020-10-14 | XCNF XGI | CLSD CNF NMAT PRC SETC | Air leaks from Comp. K6806 Auto-drain | COMPRESSOR, INST AIR COMP K-6806, OKOG1 | NG.OKOG1.K-6806-K-6806LOD | 2020-06-09 | 2020-10-14 | 2020-06-09 | 72FC | 6 | 31000167011 | 2020-04-20 | 2020-06-09 | 2020-06-09 | [5 empty] | ATLAS COPCO MODEL GA37P AIR COMPRESSOR |  | ONTR |  | 11783147 | 882716 | CM |  | 0 | 1064 | 0 | 1064
AFAINST | 22678377 | 2018-07-30 | B | 2018-07-30 | 2018-08-24 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Rectify AUTO DRAIN LEAKING ON AIR COMPRE | COMPRESSOR, INST AIR COMP K-6806, OKOG1 | NG.OKOG1.K-6806-K-6806LOD | 2018-07-30 | 2018-08-24 | 2018-07-30 | 72FC | 4 | 31000167011 | 2018-07-28 | 2018-07-30 | 2018-07-30 | [5 empty] | ATLAS COPCO MODEL GA37P AIR COMPRESSOR |  | ONTR | E | 11660291 | 766912 | CM |  | 0 | 760 | 760 | 760
AFAELEC | 22695806 | 2018-10-08 | A | 2018-10-08 |  | APPR | REL GMPS NMAT PRC SETC | Repair of faulty electric motor 37KW 1Pc | MOT,INSTR AIR COMPR PKG B,OKOG1 | NG.OKOG1.K-6808-KM6808 | 2018-10-08 |  |  | 72RE | 2 |  | 2018-10-08 | 2018-11-07 | [9 empty] | E |  | 0 | GM |  |  | 3831.12 | 3831.12 | 3831.12
AFAELEC | 22868489 | 2020-10-29 | A | 2020-10-29 | 2020-11-01 | XCNF XGI | TECO CNF GMPS NMAT PRC SETC | Un-install/install of 1pc 37Kw Mot | MOT,INSTR AIR COMPR PKG B,OKOG1 | NG.OKOG1.K-6808-KM6808 | 2020-10-29 | 2020-11-01 | 2020-10-29 | 72FC | 5 | 31000175302 | 2020-09-09 | 2020-10-29 | 2020-10-29 | [5 empty] | ATLAS COPCO,YXLA200L2,ELECTRIC MOTOR |  | ONTR | E | 11808048 | 906031 | CM |  | 0 | 878.12 | 878.12 | 878.12
AFAELEC | 22709052 | 2018-12-10 | C | 2018-12-10 | 2018-12-12 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | No power to K6807 inst air comp. | CTRL PNL,INSTR AIR COMPR PKG A | NG.OKOG1.A-6807-CP6807 | 2018-12-10 | 2018-12-12 | 2018-12-10 | 72FC | 3 | 31000175294 | 2018-12-01 | 2018-12-10 | 2018-12-10 | [5 empty] | ATLAS COPCO,GA37+,CNTRL PNL I/AIR PKG A |  | ONTR |  | 11684019 | 790409 | CM |  | 0 | 760 | 760 | 760
AFAELEC | 22879718 | 2020-12-24 | A | 2020-12-24 | 2020-12-24 | XCNF XGI | TECO CNF ESTC NMAT PRC SETC | REPLACE FAULTY CONTROL COMPONENTS ON K-6 | INSTR AIR COMPR B,I/AIR SYS,OKOG1 | NG.OKOG1.K-6808-K6808LOD | 2020-12-24 | 2020-12-24 | 2020-12-24 | 72FC | 5 | 31000175301 | 2020-11-12 | 2020-12-24 | 2020-12-24 | [5 empty] | ATLAS COPCO :GA37+,INSTRMNT AIR COMPRESR |  | ONTR | E | 11817452 | 916219 | CM |  | 0 | 1444 | 1444 | 1444
AFAELEC | 22737861 | 2019-09-16 | A | 2019-09-16 | 2020-01-31 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Stop Oil leak on air compressor K-6808 m | MOT,INSTR AIR COMPR PKG B,OKOG1 | NG.OKOG1.K-6808-KM6808 | 2019-09-16 | 2019-07-22 | 2019-09-16 | 72FC | 6 | 31000175302 | 2019-01-23 | 2019-09-16 | 2019-09-16 | [5 empty] | ATLAS COPCO,YXLA200L2,ELECTRIC MOTOR |  | ONTR |  | 11694780 | 803200 | CM |  | 0 | 462 | 456 | 924