## FGC
[5 empty] | 2018 | 2019 | 2020
|  |  |  | CM Costs | 86251.15 | 471904.83 | 26389.99
|  |  |  | CM count | 38 | 29 | 30
Failure Modes
Assets | Failure Mode | Frequency
Compressor | Valve failures -due to HH temp on disch & suctn valves | 5
| Clogged lube oil filters | 5
| Liquid Ingress | 2
| Strainer line leaking | 1
Accessories | Aux/lube oil pump - leaking externally | 3
HMI | CPU fan failure, HMI frozen & SIS value error | 5
Aftercooler | Belt cuts/failures | 35 | 39.77%
| Pillow block/fan hub/pulley failures | 13 | 14.77%
| Motor bearing failures | 12 | 13.64%
| Stator winding insulation | 4 | 4.545%
| Motor signal failures (not starting on auto/manual) | 13 | 14.77%
| Blade failure EM5603D | 1 | 1.136%
| Motor trips on demand/overload | 10 | 11.36%
| Compressor-related failures | 13
| Accessories - related failures | 3
| HMI - related failures | 5
| Aftercooler - related failures | 88

## Notifications
Priority | Notification | Breakdown | Description | Functional Location | Notification date | System status | User Status | Created On | Equipment | Maintenance Plan | Order | Priority type | Priority text | SCE Group | ABC indicator | Catalog profile | FunctLocDescrip. | Object Description | Completion by date | Master insp.charac. | Notification type
3 | 11814546 | X | 1st stge air cooler fan EM5601B belt cut | NG.AFA.OKOG1.GC.E-5601 | 2020-10-13 | NOCO ORAS | CLSD | 2020-10-13 | 31000137057 |  | 22873959 | CM | Complete by 2 Weeks | PC002 | A | CP_STA502 | STG1 AFTR COOLR, GAS COMPR SYS, OKOG1 | NUOVO PIGNONE STG1 AFTR COOLR | 2020-10-22 |  | Z1
3 | 11814232 | X | 2nd stge air cooler fan EM5602B belt cut | NG.AFA.OKOG1.GC.E-5602 | 2020-10-11 | NOCO ORAS | CLSD | 2020-10-11 | 31000137058 |  | 22873732 | CM | Complete by 2 Weeks | PC002 | A | CP_STA502 | STG2 AFTR COOLR, GAS COMPR SYS, OKOG1 | NUOVO PIGNONE STG2 AFTR COOLR | 2020-10-20 |  | Z1
4 | 11739984 | X | 3rd stg Air cooler fan EM5603C belt cut | NG.AFA.OKOG1.GC.E-5603 | 2019-09-10 | NOCO ORAS | CLSD | 2019-09-10 | 31000137059 |  | 22783044 | CM | Complete by 4 Weeks | PC002 | A | CP_STA502 | STG3 AFTR COOLR, GAS COMPR SYS, OKOG1 | NUOVO PIGNONE STG3 AFTR COOLR | 2019-09-19 |  | Z1
4 | 11741620 | X | 4th Stg discharge cooler fan A belt cut | NG.OKOG1.E-5604-E-5604FAN | 2019-09-16 | NOCO ORAS | CLSD | 2019-09-16 | 31000137442 |  | 22784203 | CM | Complete by 4 Weeks |  | B | CP_ROT104 | FAN, E-5604, GAS COMPR SYS, OKOG1 | MOORE FANS FAN | 2019-09-25 |  | Z1
5 | 11660784 | X | CUT AND LOOSE FAN BELT ON E-5605A | NG.OKOG1.E-5605-E-5605FAN | 2018-07-30 | NOCO ORAS | CLSD | 2018-07-30 | 31000137443 |  | 22679227 | CM | Complete by 8 Weeks |  | B | CP_ROT104 | FAN, E-5605, GAS COMPR SYS, OKOG1 | NUOVO PIGNONE FAN | 2018-08-17 |  | Z1
2 | 11707648 | X | Cut belt on FGC aftercooler E-5603C | NG.OKOG1.E-5603-E-5603FAN | 2019-04-01 | NOCO ORAS | CLSD | 2019-04-01 | 31000137441 |  | 22750164 | CM | Complete by 1 Week |  | B | CP_ROT104 | FAN, E-5603, GAS COMPR SYS, OKOG1 | MOORE FANS FAN | 2019-04-03 |  | Z1
4 | 11807765 | X | CUT FAN BELT ON AFTERCOOLER EM-5603C. | NG.OKOG1.E-5603-E-5603FAN | 2020-09-05 | NOCO ORAS | CLSD | 2020-09-05 | 31000137441 |  | 22868173 | CM | Complete by 4 Weeks |  | B | CP_ROT104 | FAN, E-5603, GAS COMPR SYS, OKOG1 | MOORE FANS FAN | 2020-10-18 |  | Z1
2 | 11771089 | X | Cut Fan belt on E-5601A | NG.OKOG1.E-5601-EM-5601A | 2020-02-10 | NOCO ORAS | CLSD | 2020-02-10 | 31000137086 |  | 22821653 | CM | Complete by 1 Week | IC003 | A | CP_ELE301 | MOTOR, E-5601, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2020-02-14 |  | Z1
3 | 11787177 | X | Cut fan belt on E-5601B | NG.OKOG1.E-5601-EM-5601B | 2020-05-14 | NOCO ORAS | CLSD | 2020-05-14 |  |  | 22845503 | CM | Complete by 2 Weeks | IC003 | A | CP_ELE301 | MOTOR, E-5601, GAS COMPR SYS, OKOG1 |  | 2020-05-28 |  | Z1
3 | 11748365 | X | Cut Fan Belt on E-5603C & D | NG.OKOG1.E-5603-E-5603FAN | 2019-10-15 | NOCO ORAS | CLSD | 2019-10-15 | 31000137441 |  | 22790514 | CM | Complete by 2 Weeks |  | B | CP_ROT104 | FAN, E-5603, GAS COMPR SYS, OKOG1 | MOORE FANS FAN | 2019-10-29 |  | Z1
4 | 11726689 | X | Cut fan belt on EM5601A | NG.OKOG1.E-5601-E-5601FAN | 2019-07-05 | NOCO ORAS | CLSD | 2019-07-05 | 31000137439 |  | 22769043 | CM | Complete by 4 Weeks |  | B | CP_ROT104 | FAN, E-5601, GAS COMPR SYS, OKOG1 | MOORE FANS FAN | 2019-07-06 |  | Z1
2 | 11665410 | X | Cut fan belt on EM5601B | NG.AFA.OKOG1.GC.E-5601 | 2018-08-22 | NOCO ORAS | CLSD | 2018-08-22 | 31000137057 |  | 22685146 | CM | Complete by 1 Week | PC002 | A | CP_STA502 | STG1 AFTR COOLR, GAS COMPR SYS, OKOG1 | NUOVO PIGNONE STG1 AFTR COOLR | 2018-08-26 |  | Z1
4 | 11794886 | X | Cut fan belt on EM5601B | NG.OKOG1.E-5604-EM-5604B | 2020-06-27 | NOCO ORAS | CLSD | 2020-06-27 |  |  | 22854203 | CM | Complete by 4 Weeks | IC003 | A | CP_ELE301 | MOTOR, E-5604, GAS COMPR SYS, OKOG1 |  | 2020-07-15 |  | Z1
3 | 11785238 |  | Cut Fan belt on EM-5603C | NG.OKOG1.E-5603-E-5603FAN | 2020-05-02 | NOCO ORAS | CLSD | 2020-05-02 | 31000137441 |  | 22841739 | CM | Complete by 2 Weeks |  | B | CP_ROT104 | FAN, E-5603, GAS COMPR SYS, OKOG1 | MOORE FANS FAN | 2020-05-10 |  | Z1
2 | 11720730 | X | Cut fan belt on FGC 1st Stage E-5601B | NG.OKOG1.E-5601-EM-5601B | 2019-06-07 | NOCO ORAS | CLSD | 2019-06-07 |  |  | 22763787 | CM | Complete by 1 Week | IC003 | A | CP_ELE301 | MOTOR, E-5601, GAS COMPR SYS, OKOG1 |  | 2019-06-07 |  | Z1
5 | 11762994 | X | Cut Fan Belt on FGC Cooler EM-5601B | NG.OKOG1.E-5601-E-5601FAN | 2019-12-31 | NOCO ORAS | CLSD | 2019-12-31 | 31000137439 |  | 22808738 | CM | Complete by 8 Weeks |  | B | CP_ROT104 | FAN, E-5601, GAS COMPR SYS, OKOG1 | MOORE FANS FAN | 2020-01-08 |  | Z1
5 | 11810389 | X | Cut fan belt on FGC EM-5601A cooler fan | NG.OKOG1.E-5601-E-5601FAN | 2020-09-20 | NOCO ORAS | CLSD | 2020-09-20 | 31000137439 |  | 22870373 | CM | Complete by 8 Weeks |  | B | CP_ROT104 | FAN, E-5601, GAS COMPR SYS, OKOG1 | MOORE FANS FAN | 2020-10-18 |  | Z1
2 | 11811004 | X | Cut fan belt on FGC EM-5601B cooler fan | NG.OKOG1.E-5601-E-5601FAN | 2020-09-23 | NOCO ORAS | CLSD | 2020-09-23 | 31000137439 |  | 22871066 | CM | Complete by 1 Week |  | B | CP_ROT104 | FAN, E-5601, GAS COMPR SYS, OKOG1 | MOORE FANS FAN | 2020-10-01 |  | Z1
6 | 11819607 |  | Cut fan belt on FGC EM-5602A Cooler Fan | NG.OKOG1.E-5602-E-5602FAN | 2020-11-09 | NOPR ORAS | TBCO | 2020-11-09 | 31000137440 |  | 22879290 | CM | Complete by 6 Months |  | B | CP_ROT104 | FAN, E-5602, GAS COMPR SYS, OKOG1 | MOORE FANS FAN |  |  | Z1
5 | 11810548 |  | Cut fan belt on FGC EM-5602B cooler fan | NG.OKOG1.E-5602-E-5602FAN | 2020-09-21 | NOCO ORAS | CLSD | 2020-09-21 | 31000137440 |  | 22870374 | CM | Complete by 8 Weeks |  | B | CP_ROT104 | FAN, E-5602, GAS COMPR SYS, OKOG1 | MOORE FANS FAN | 2020-11-03 |  | Z1
5 | 11798162 | X | Cut fan belt on FGC EM-5603C cooler fan | NG.OKOG1.E-5603-E-5603FAN | 2020-07-15 | NOCO ORAS | CLSD | 2020-07-15 | 31000137441 |  | 22858044 | CM | Complete by 8 Weeks |  | B | CP_ROT104 | FAN, E-5603, GAS COMPR SYS, OKOG1 | MOORE FANS FAN | 2020-07-28 |  | Z1
4 | 11630527 | X | Damaged Fan belt on E-5603C @ FGC | NG.AFA.OKOG1.GC.E-5603 | 2018-03-13 | NOCO ORAS | CLSD | 2018-03-13 | 31000137059 |  | 22645762 | CM | Complete by 4 Weeks | PC002 | A | CP_ROT104 | STG3 AFTR COOLR, GAS COMPR SYS, OKOG1 | NUOVO PIGNONE STG3 AFTR COOLR | 2018-03-20 |  | Z1
5 | 11695419 |  | FGC 1st stage damaged fan belt | NG.OKOG1.E-5601-E-5601FAN | 2019-01-26 | NOCO ORAS | CLSD | 2019-01-26 | 31000137439 |  | 22738288 | CM | Complete by 8 Weeks |  | B | CP_ROT104 | FAN, E-5601, GAS COMPR SYS, OKOG1 | MOORE FANS FAN | 2019-02-02 |  | Z1
4 | 11712724 | X | E-5603C Drive Belt snapped off | NG.OKOG1.E-5603-E-5603FAN | 2019-04-27 | NOCO ORAS | CLSD | 2019-04-27 | 31000137441 |  | 22756013 | CM | Complete by 4 Weeks |  | B | CP_ROT104 | FAN, E-5603, GAS COMPR SYS, OKOG1 | MOORE FANS FAN | 2019-05-24 |  | Z1
1 | 11677073 | X | Fan belt on FGC EM5601A cut | NG.AFA.OKOG1.GC.E-5601 | 2018-10-24 | NOCO ORAS | CLSD | 2018-10-24 | 31000137057 |  | 22699693 | CM | Immediate Start | PC002 | A | CP_STA502 | STG1 AFTR COOLR, GAS COMPR SYS, OKOG1 | NUOVO PIGNONE STG1 AFTR COOLR | 2018-10-25 |  | Z1
5 | 11764939 | X | FGC 1st Stg Cooler Fan Belt EM5601B cut | NG.OKOG1.E-5601-EM-5601B | 2020-01-10 | NOCO ORAS | CLSD | 2020-01-10 |  |  | 22811248 | CM | Complete by 8 Weeks | IC003 | A | CP_ELE301 | MOTOR, E-5601, GAS COMPR SYS, OKOG1 |  | 2020-01-15 |  | Z1
4 | 11668279 |  | Replace Drive Belt on E-5603B | NG.OKOG1.E-5603-E-5603FAN | 2018-09-06 | NOCO ORAS | CLSD | 2018-09-06 | 31000137441 |  | 22688699 | CM | Complete by 4 Weeks |  | B | CP_ROT104 | FAN, E-5603, GAS COMPR SYS, OKOG1 | MOORE FANS FAN | 2018-09-08 |  | Z1
6 | 11789907 | X | Slipped Drive Fan Belt on E-5605B | NG.OKOG1.E-5605-E-5605FAN | 2020-05-30 | NOCO ORAS | CLSD | 2020-05-30 | 31000137443 |  | 22847726 | CM | Complete by 6 Months |  | B | CP_ROT104 | FAN, E-5605, GAS COMPR SYS, OKOG1 | NUOVO PIGNONE FAN | 2020-07-27 |  | Z1
3 | 11807519 | X | Stage 3 aftercooler EM5603C fan belt cut | NG.AFA.OKOG1.GC.E-5603 | 2020-09-03 | NOCO ORAS | CLSD | 2020-09-03 | 31000137059 |  | 22868172 | CM | Complete by 2 Weeks | PC002 | A | CP_STA502 | STG3 AFTR COOLR, GAS COMPR SYS, OKOG1 | NUOVO PIGNONE STG3 AFTR COOLR | 2020-09-25 |  | Z1
4 | 11813906 | X | stage 3 air cooler EM5603C fan belt cut | NG.AFA.OKOG1.GC.E-5603 | 2020-10-09 | NOCO ORAS | CLSD | 2020-10-09 | 31000137059 |  | 22873437 | CM | Complete by 4 Weeks | PC002 | A | CP_STA502 | STG3 AFTR COOLR, GAS COMPR SYS, OKOG1 | NUOVO PIGNONE STG3 AFTR COOLR | 2020-10-26 |  | Z1
4 | 11813893 | X | stage 3 air cooler EM5603D fan belt cut | NG.OKOG1.E-5603-E-5603FAN | 2020-10-09 | NOPR ORAS | TBCO | 2020-10-09 | 31000137441 |  | 22873436 | CM | Complete by 4 Weeks |  | B | CP_ROT104 | FAN, E-5603, GAS COMPR SYS, OKOG1 | MOORE FANS FAN |  |  | Z1
2 | 11668003 | X | EM5603B fan belt fall from position | NG.OKOG1.E-5603-EM-5603B | 2018-09-05 | NOCO NOPT ORAS | CLSD | 2018-09-05 | 31000137095 |  | 22688891 | CM | Complete by 1 Week | IC003 | A | CP_ELE301 | MOTOR, E-5603, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2018-09-17 |  | Z1
5 | 11697903 | X | Worn Drive Belt on E-5601B | NG.OKOG1.E-5601-E-5601FAN | 2019-02-06 | NOCO ORAS | CLSD | 2019-02-06 | 31000137439 |  | 22740093 | CM | Complete by 8 Weeks |  | B | CP_ROT104 | FAN, E-5601, GAS COMPR SYS, OKOG1 | MOORE FANS FAN | 2019-02-12 |  | Z1
4 | 11690175 |  | Worn Drive Belt on E-5602B | NG.AFA.OKOG1.GC.E-5602 | 2018-12-31 | NOCO ORAS | CLSD | 2018-12-31 | 31000137058 |  | 22733585 | CM | Complete by 4 Weeks | PC002 | A | CP_ROT104 | STG2 AFTR COOLR, GAS COMPR SYS, OKOG1 | NUOVO PIGNONE STG2 AFTR COOLR | 2019-01-07 |  | Z1
5 | 11675630 | X | Belt pull out on Cooler Motor EM-5601B | NG.OKOG1.E-5601-EM-5601B | 2018-10-16 | NOCO ORAS | CLSD | 2018-10-16 |  |  | 22698275 | CM | Complete by 8 Weeks | IC003 | A | CP_ELE301 | MOTOR, E-5601, GAS COMPR SYS, OKOG1 |  | 2018-12-01 |  | Z1
4 | 11814667 |  | 1st stag coolr fan EM5601A unusual noise | NG.AFA.OKOG1.GC.E-5601 | 2020-10-13 | NOCO ORAS | CLSD | 2020-10-13 | 31000137057 |  | 22874435 | CM | Complete by 4 Weeks | PC002 | A | CP_STA502 | STG1 AFTR COOLR, GAS COMPR SYS, OKOG1 | NUOVO PIGNONE STG1 AFTR COOLR | 2020-10-28 |  | Z1
4 | 11813047 | X | 1st stag coolr fan EM5601B unusual noise | NG.AFA.OKOG1.GC.E-5601 | 2020-10-04 | NOCO ORAS | CLSD | 2020-10-04 | 31000137057 |  | 22872415 | CM | Complete by 4 Weeks | PC002 | A | CP_STA502 | STG1 AFTR COOLR, GAS COMPR SYS, OKOG1 | NUOVO PIGNONE STG1 AFTR COOLR | 2020-10-18 |  | Z1
6 | 11629379 |  | EM 5603A making unusual noise | NG.OKOG1.E-5603-EM-5603A | 2018-03-08 | NOCO ORAS | CLSD | 2018-03-08 | 31000137094 |  | 22644257 | CM | Complete by 6 Months | IC003 | A | CP_ELE301 | MOTOR, E-5603, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2018-04-23 |  | Z1
3 | 11629380 | X | EM 5606A making unusual noise | NG.OKOG1.E-5606-EM-5606A | 2018-03-08 | NOCO ORAS | CLSD | 2018-03-08 | 31000137103 |  | 22644258 | CM | Complete by 2 Weeks | IC003 | A | CP_ELE301 | MOTOR, E-5606, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2018-05-02 |  | Z1
6 | 11807021 |  | FGC making unusual noise from stage 4 | NG.AFA.OKOG1.GC.K-5601 | 2020-09-01 | NOCO ORAS | CLSD | 2020-09-01 |  |  | 22868177 | CM | Complete by 6 Months | PC003 | A | CP_ROT102 | FLSH GAS COMPR, GAS COMPR SYS, OKOG1 |  | 2020-09-27 |  | Z1
4 | 11649888 | X | Unusual noise on 2nd stage fan EM-5602A | NG.OKOG1.E-5602-EM-5602A | 2018-06-06 | NOCO ORAS | CLSD | 2018-06-06 | 31000137089 |  | 22666756 | CM | Complete by 4 Weeks | IC003 | A | CP_ELE301 | MOTOR, E-5602, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2018-08-31 |  | Z1
2 | 11823870 |  | Unusual noise on 3rd stage fan EM5603A | NG.OKOG1.E-5603-EM-5603A | 2020-12-01 | NOCO ORAS | CLSD | 2020-12-01 | 31000137095 |  | 22885005 | CM | Complete by 1 Week | IC003 | A | CP_ELE301 | MOTOR, E-5603, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2020-12-16 |  | Z1
4 | 11668012 |  | Unusual noise from EM5603A | NG.OKOG1.E-5603-EM-5603A | 2018-09-05 | NOCO NOPT ORAS | CLSD | 2018-09-05 | 31000137094 |  | 22688890 | CM | Complete by 4 Weeks | IC003 | A | CP_ELE301 | MOTOR, E-5603, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2018-09-22 |  | Z1
7 | 11771754 |  | Wobbling Fan Block/Pulley on E-5601A | NG.OKOG1.E-5601-E-5601FAN | 2020-02-13 | NOCO ORAS | CLSD | 2020-02-13 | 31000137439 |  | 22823059 | CM | Complete by 12 Mths |  | B | CP_ROT104 | FAN, E-5601, GAS COMPR SYS, OKOG1 | MOORE FANS FAN | 2020-07-27 |  | Z1
5 | 11771105 |  | Broken motor pulley belt guard E-5601B | NG.OKOG1.E-5601-EM-5601B | 2020-02-10 | NOCO ORAS | CLSD | 2020-02-10 |  |  | 22821654 | CM | Complete by 8 Weeks | IC003 | A | CP_ELE301 | MOTOR, E-5601, GAS COMPR SYS, OKOG1 |  | 2020-02-19 |  | Z1
5 | 11675841 | X | High vibration on E-5603B Assembly | NG.OKOG1.E-5603-E-5603FAN | 2018-10-17 | NOCO ORAS | CLSD | 2018-10-17 | 31000137441 |  | 22698805 | CM | Complete by 8 Weeks |  | B | CP_ROT104 | FAN, E-5603, GAS COMPR SYS, OKOG1 | MOORE FANS FAN | 2018-12-05 |  | Z1
4 | 11670857 | X | High vibration on EM-5603B | NG.OKOG1.E-5603-EM-5603B | 2018-09-21 | NOCO NOPT ORAS | CLSD | 2018-09-21 | 31000137095 |  | 22693218 | CM | Complete by 4 Weeks | IC003 | A | CP_ELE301 | MOTOR, E-5603, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2018-10-17 |  | Z1
6 | 11762670 | X | EM 5605B FAIL TO RUN ON AUTO/MAN MODE | NG.OKOG1.E-5605-56HS652BA | 2019-12-29 | NOCO ORAS | CLSD | 2019-12-29 |  |  | 22808729 | CM | Complete by 6 Months |  | B | CP_INS202 | RCU, EM-5605B, GAS COMPR SYS, OKOG1 |  | 2020-01-08 |  | Z1
5 | 11745570 |  | EM5601A not starting on Auto | NG.OKOG1.E-5601-EM-5601A | 2019-10-03 | NOCO ORAS | CLSD | 2019-10-03 | 31000137086 |  | 22787600 | CM | Complete by 8 Weeks | IC003 | A | CP_ELE301 | MOTOR, E-5601, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2019-10-19 |  | Z1
5 | 11745571 |  | EM5602A not starting on Auto | NG.OKOG1.E-5602-EM-5602A | 2019-10-03 | NOCO ORAS | CLSD | 2019-10-03 | 31000137089 |  | 22787601 | CM | Complete by 8 Weeks | IC003 | A | CP_ELE301 | MOTOR, E-5602, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2019-10-21 |  | Z1
5 | 11745572 |  | EM5603A not starting on Auto | NG.OKOG1.E-5603-EM-5603A | 2019-10-03 | NOCO ORAS | CLSD | 2019-10-03 | 31000137095 |  | 22787603 | CM | Complete by 8 Weeks | IC003 | A | CP_ELE301 | MOTOR, E-5603, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2019-10-21 |  | Z1
5 | 11745574 |  | EM5603B not starting on Auto | NG.OKOG1.E-5603-EM-5603B | 2019-10-03 | NOCO ORAS | CLSD | 2019-10-03 | 31000137094 |  | 22787602 | CM | Complete by 8 Weeks | IC003 | A | CP_ELE301 | MOTOR, E-5603, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2019-11-25 |  | Z1
5 | 11745578 |  | EM5604 not starting on Auto | NG.OKOG1.E-5604-EM-5604A | 2019-10-03 | NOCO ORAS | CLSD | 2019-10-03 | 31000137099 |  | 22787604 | CM | Complete by 8 Weeks | IC003 | A | CP_ELE301 | MOTOR, E-5604, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2019-11-25 |  | Z1
6 | 11786418 | X | EM5604A not running on manual | NG.OKOG1.E-5604-EM-5604A | 2020-05-11 | NOCO ORAS | CLSD | 2020-05-11 | 31000137099 |  | 22843566 | CM | Complete by 6 Months | IC003 | A | CP_ELE301 | MOTOR, E-5604, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2020-07-03 |  | Z1
6 | 11744369 |  | EM5605A not starting on Auto | NG.OKOG1.E-5605-EM-5605A | 2019-09-27 | NOCO ORAS | CLSD | 2019-09-27 | 31000137101 |  | 22786230 | CM | Complete by 6 Months | IC003 | A | CP_ELE301 | MOTOR, E-5605, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2020-01-27 |  | Z1
5 | 11742656 |  | FGC 4th stage fan B not starting on Auto | NG.OKOG1.E-5604-RCUEM5604B | 2019-09-19 | NOCO ORAS | CLSD | 2019-09-19 |  |  | 22784946 | CM | Complete by 8 Weeks |  | B | CP_ELE302 | RCU, E-5604, GAS COMPR SYS, OKOG1 |  | 2019-10-11 |  | Z1
6 | 11747549 | X | FGC Lube Oil Fan A not running on Auto | NG.OKOG1.E-5605-RCUEM5605A | 2019-10-11 | NOCO ORAS | CLSD | 2019-10-11 |  |  | 22789413 | CM | Complete by 6 Months |  | B | CP_INS202 | RCU, E-5605, GAS COMPR SYS, OKOG1 |  | 2020-01-15 |  | Z1
5 | 11641573 |  | EM-5601A TRIPS ON OVERLOAD ON STARTING | NG.OKOG1.E-5601-EM-5601A | 2018-05-03 | NOCO ORAS | CLSD | 2018-05-03 | 31000137086 |  | 22658797 | CM | Complete by 8 Weeks | IC003 | A | CP_ELE301 | MOTOR, E-5601, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2019-01-07 |  | Z1
2 | 11646788 | X | EM-5601B Trip on stalled motor fault. | NG.OKOG1.E-5601-EM-5601B | 2018-05-25 | NOCO ORAS | CLSD | 2018-05-25 |  |  | 22663329 | CM | Complete by 1 Week | IC003 | A | CP_ELE301 | MOTOR, E-5601, GAS COMPR SYS, OKOG1 |  | 2018-05-31 |  | Z1
3 | 11637488 |  | Fan Motor EM5606B tripping @ FGC tempere | NG.OKOG1.E-5606-EM-5606B | 2018-04-15 | NOCO ORAS | CLSD | 2018-04-15 | 31000137104 |  | 22653641 | CM | Complete by 2 Weeks | IC003 | A | CP_ELE301 | MOTOR, E-5606, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2018-04-23 |  | Z1
5 | 11666144 |  | FGC 4th Stg EM-5604A trips on demand. | NG.OKOG1.E-5604-EM-5604A | 2018-08-27 | NOCO NOPT ORAS | CLSD | 2018-08-27 | 31000137099 |  | 22686251 | CM | Complete by 8 Weeks | IC003 | A | CP_ELE301 | MOTOR, E-5604, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2018-10-13 |  | Z1
6 | 11688584 | X | FGC 4th Stg EM-5604A trips on Overload. | NG.OKOG1.E-5604-EM-5604A | 2018-12-21 | NOCO ORAS | CLSD | 2018-12-21 | 31000137099 |  | 22714153 | CM | Complete by 6 Months | IC003 | A | CP_ELE301 | MOTOR, E-5604, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2019-06-13 |  | Z1
1 | 11715823 | X | FGC EM5606B trips on overload | NG.OKOG1.E-5606-EM-5606B | 2019-05-12 | NOCO ORAS | CLSD | 2019-05-12 | 31000137104 |  | 22759724 | CM | Immediate Start | IC003 | A | CP_ELE301 | MOTOR, E-5606, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2019-06-08 |  | Z1
6 | 11635781 | X | Incessant trip of elect motor EM-5603B | NG.OKOG1.E-5603-EM-5603B | 2018-04-07 | NOCO ORAS | CLSD | 2018-04-07 | 31000137095 |  | 22651767 | CM | Complete by 6 Months | IC003 | A | CP_ELE301 | MOTOR, E-5603, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2018-06-06 |  | Z1
3 | 11617292 | X | Tempered H2O cooler fan, EM-5606B tripp | NG.OKOG1.E-5606-EM-5606B | 2018-01-13 | NOCO NOPT ORAS | CLSD | 2018-01-13 | 31000137104 |  | 22630423 | CM | Complete by 2 Weeks | IC003 | A | CP_ELE301 | MOTOR, E-5606, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2018-03-29 |  | Z1
3 | 11638113 | X | TRIPPING FAULT ON EM-5602A FGC COOLER | NG.OKOG1.E-5602-EM-5602A | 2018-04-17 | NOCO ORAS | CLSD | 2018-04-17 | 31000137089 |  | 22654171 | CM | Complete by 2 Weeks | IC003 | A | CP_ELE301 | MOTOR, E-5602, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2018-06-04 |  | Z1
3 | 11637074 | X | TRIPPING FAULT ON EM-5603A FGC COOLER | NG.OKOG1.E-5603-EM-5603A | 2018-04-12 | NOCO ORAS | CLSD | 2018-04-12 | 31000137094 |  | 22653045 | CM | Complete by 2 Weeks | IC003 | A | CP_ELE301 | MOTOR, E-5603, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2018-07-31 |  | Z1
3 | 11659520 | X | FGC Cooler Fan E-5601A suspected faulty | NG.OKOG1.E-5601-E-5601FAN | 2018-07-23 | NOCO ORAS | CLSD | 2018-07-23 | 31000137439 |  | 22677665 | CM | Complete by 2 Weeks |  | B | CP_ROT104 | FAN, E-5601, GAS COMPR SYS, OKOG1 | MOORE FANS FAN | 2018-08-06 |  | Z1
6 | 11659524 |  | FGC Cooler Fan E-5602A suspected faulty | NG.OKOG1.E-5602-E-5602FAN | 2018-07-23 | NOCO ORAS | CLSD | 2018-07-23 | 31000137440 |  | 22677666 | CM | Complete by 6 Months |  | B | CP_ROT104 | FAN, E-5602, GAS COMPR SYS, OKOG1 | MOORE FANS FAN | 2018-12-03 |  | Z1
6 | 11659528 |  | FGC Cooler Fan E-5603A suspected faulty | NG.OKOG1.E-5603-E-5603FAN | 2018-07-23 | NOCO ORAS | CLSD | 2018-07-23 | 31000137441 |  | 22677667 | CM | Complete by 6 Months |  | B | CP_ROT104 | FAN, E-5603, GAS COMPR SYS, OKOG1 | MOORE FANS FAN | 2018-08-21 |  | Z1
6 | 11747551 |  | FGC Cooling Water Fan A signal fault | NG.OKOG1.E-5606-EM-5606A | 2019-10-11 | NOCO ORAS | CLSD | 2019-10-11 | 31000137103 |  | 22789414 | CM | Complete by 6 Months | IC003 | A | CP_ELE301 | MOTOR, E-5606, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2020-01-15 |  | Z1
3 | 11715822 | X | EM5606A fail to start CFA feedback error | NG.OKOG1.E-5606-EM-5606A | 2019-05-12 | NOCO ORAS | CLSD | 2019-05-12 | 31000137103 |  | 22759766 | CM | Complete by 2 Weeks | IC003 | A | CP_ELE301 | MOTOR, E-5606, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2019-05-21 |  | Z1
3 | 11766471 | X | EM5606A FAULT_ALM | NG.OKOG1.E-5606-EM-5606A | 2020-01-18 | NOCO ORAS | CLSD | 2020-01-18 | 31000137103 |  | 22812962 | CM | Complete by 2 Weeks | IC003 | A | CP_ELE301 | MOTOR, E-5606, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2020-01-27 |  | Z1
5 | 11674460 | X | Faulty FGC cooler motor EM-5602A | NG.OKOG1.E-5602-EM-5602A | 2018-10-09 | NOCO ORAS | CLSD | 2018-10-09 | 31000137089 |  | 22696451 | CM | Complete by 8 Weeks | IC003 | A | CP_ELE301 | MOTOR, E-5602, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2018-11-01 |  | Z1
6 | 11720758 | X | FGC 1st Stage EM-5601A failed on demand | NG.OKOG1.E-5601-EM-5601A | 2019-06-07 | NOCO ORAS | CLSD | 2019-06-07 | 31000137086 |  | 22764126 | CM | Complete by 6 Months | IC003 | A | CP_ELE301 | MOTOR, E-5601, GAS COMPR SYS, OKOG1 | ELECTRIC MOTOR | 2019-07-17 |  | Z1
4 | 11639747 |  | Clogged F-5601A Lube oil Filter | NG.AFA.OKOG1.GC.F-5601A | 2018-04-25 | NOCO ORAS | CLSD | 2018-04-25 | 31000137446 |  | 22656068 | CM | Complete by 4 Weeks |  | C | CP_MEC401 | L/OIL FLTR A, GAS COMPR SYS, OKOG1 | FILTERSD6PW43F30F01/RC026039L/OIL FLTR | 2018-05-08 |  | Z1
4 | 11639744 |  | Clogged F-5601B Lube oil Filter | NG.AFA.OKOG1.GC.F-5601B | 2018-04-25 | NOCO ORAS | CLSD | 2018-04-25 | 31000137447 |  | 22656070 | CM | Complete by 4 Weeks |  | C | CP_MEC401 | L/OIL FLTR B, GAS COMPR SYS, OKOG1 | FILTERS L/OIL FLTR B | 2018-05-08 |  | Z1
3 | 11660276 |  | FGC LUBE OIL FILTER F-5601A HIGH DP | NG.AFA.OKOG1.GC.F-5601A | 2018-07-27 | NOCO ORAS | CLSD | 2018-07-27 | 31000137446 |  | 22678386 | CM | Complete by 2 Weeks |  | C | CP_MEC401 | L/OIL FLTR A, GAS COMPR SYS, OKOG1 | FILTERSD6PW43F30F01/RC026039L/OIL FLTR | 2018-08-06 |  | Z1
3 | 11660277 |  | FGC LUBE OIL FILTER F-5601B HIGH DP | NG.AFA.OKOG1.GC.F-5601B | 2018-07-27 | NOCO ORAS | CLSD | 2018-07-27 | 31000137447 |  | 22678387 | CM | Complete by 2 Weeks |  | C | CP_MEC401 | L/OIL FLTR B, GAS COMPR SYS, OKOG1 | FILTERS L/OIL FLTR B | 2018-08-04 |  | Z1
6 | 11819881 |  | High DP on lube oil filter at FGC unit | NG.AFA.OKOG1.GC.F-5601A | 2020-11-10 | NOPR ORAS | APPR | 2020-11-10 | 31000137446 |  | 22880838 | CM | Complete by 6 Months |  | C | CP_MEC401 | L/OIL FLTR A, GAS COMPR SYS, OKOG1 | FILTERSD6PW43F30F01/RC026039L/OIL FLTR |  |  | Z1
2 | 11730797 |  | FGC 3rd stge inlet Strainer line leaking | NG.AFA.OKOG1.GC.V-5603 | 2019-07-26 | NOCO ORAS | CLSD | 2019-07-26 | 31000137347 |  | 22773428 | CM | Complete by 1 Week | PC001 | A | CP_STA506 | STG 3 S/SCRUB, GAS COMPR SYS, OKOG1 | CMS SRL STG 3 S/SCRUB | 2019-08-08 |  | Z1
2 | 11673457 | X | FGC Tripping on HH Temp 3rd Stage | NG.OKOG1.K-5601-K-5601LOD | 2018-10-04 | NOCO ORAS | CLSD | 2018-10-04 | 31000137111 |  | 22695401 | CM | Complete by 1 Week | PC003 | A | CP_ROT102 | COMP, K-5601, GAS COMPR SYS, OKOG1 | NUOVO PIGNONE FLASH GAS COMPRESSOR K-560 | 2018-10-07 |  | Z1
2 | 11657620 |  | FGC Tripping on HH Temp 3rd Stage | NG.OKOG1.K-5601-K-5601LOD | 2018-07-13 | NOCO ORAS | CLSD | 2018-07-13 | 31000137111 |  | 22674903 | CM | Complete by 1 Week | PC003 | A | CP_ROT102 | COMP, K-5601, GAS COMPR SYS, OKOG1 | NUOVO PIGNONE FLASH GAS COMPRESSOR K-560 | 2018-07-15 |  | Z1
2 | 11659347 | X | FGC Trips on HH 1st Stage Discharge Temp | NG.OKOG1.E-5601-E-5601FAN | 2018-07-21 | NOCO ORAS | CLSD | 2018-07-22 | 31000137439 |  | 22676901 | CM | Complete by 1 Week |  | B | CP_ROT104 | FAN, E-5601, GAS COMPR SYS, OKOG1 | MOORE FANS FAN | 2018-07-26 |  | Z1
6 | 11713469 |  | Hi Temp. on FGC 3rd Stg Valves | NG.OKOG1.K-5601-K-5601LOD | 2019-04-29 | NOCO NOPT ORAS | CLSD | 2019-04-29 | 31000137111 |  | 22756581 | CM | Complete by 6 Months | PC003 | A | CP_ROT102 | COMP, K-5601, GAS COMPR SYS, OKOG1 | NUOVO PIGNONE FLASH GAS COMPRESSOR K-560 | 2019-05-22 |  | Z1
4 | 11739540 |  | FGC HMI CPU fan failed | NG.AFA.OKOG1.GC.CP-5601 | 2019-09-08 | NOCO ORAS | CLSD | 2019-09-08 | 31000136996 |  | 22782550 | CM | Complete by 4 Weeks |  | B | CP_INS203 | F/GAS COMP C/PANLCP-5601, GAS COMPSYS, O | F/GAS COMPR CONTROL PANEL | 2019-09-23 |  | Z1
5 | 11738880 |  | FGC HMI frozen | NG.AFA.OKOG1.GC.K-5601 | 2019-09-04 | NOCO ORAS | CLSD | 2019-09-04 |  |  | 22781962 | CM | Complete by 8 Weeks | PC003 | A | CP_ROT102 | FLSH GAS COMPR, GAS COMPR SYS, OKOG1 |  | 2019-09-19 |  | Z1
5 | 11813750 |  | FGC SIS trip settings default to zero | NG.AFA.OKOG1.GC | 2020-10-08 | NOPR ORAS | APPR | 2020-10-08 |  |  | 22873147 | CM | Complete by 8 Weeks |  | B | NO_MAINT1 | GAS COMPR SYS, OKOG1 |  |  |  | Z1
5 | 11766954 |  | PV BAD IOF on 56PDI371 | NG.AFA.OKOG1.GC | 2020-01-20 | NOCO ORAS | CLSD | 2020-01-21 |  |  | 22813773 | CM | Complete by 8 Weeks |  | B | NO_MAINT1 | GAS COMPR SYS, OKOG1 |  | 2020-01-27 |  | Z1
5 | 11733349 |  | Rod-drop Data Streaming Fault, Stg2 FGC | NG.OKOG1.K-5601-56ZT634 | 2019-08-08 | NOCO ORAS | CLSD | 2019-08-08 |  |  | 22776184 | CM | Complete by 8 Weeks |  | C | CP_INS202 | POS TRANS, K-5601, GAS COMPR SYS, OKOG1 |  | 2019-09-01 |  | Z1
7 | 11827755 |  | Fan blade defective on EM-5603D | NG.OKOG1.E-5603-E-5603FAN | 2020-12-21 | NOPR ORAS | APPR | 2020-12-21 | 31000137441 |  | 22888725 | CM | Complete by 12 Mths |  | B | CP_ROT104 | FAN, E-5603, GAS COMPR SYS, OKOG1 | MOORE FANS FAN |  |  | Z1
6 | 11632675 |  | FGC 4th stage scrubber sight glass fault | NG.OKOG1.V-5604-56LG351 | 2018-03-23 | NOCO ORAS | CLSD | 2018-03-23 |  |  | 22648196 | CM | Complete by 6 Months |  | C | CP_INS202 | LG, V-5604, GAS COMPR SYS, OKOG1 |  | 2018-09-18 |  | Z1
3 | 11764985 |  | FGC NDE lube oil sight glass leaking | NG.AFA.OKOG1.GC.K-5601 | 2020-01-10 | NOCO ORAS | CLSD | 2020-01-10 |  |  | 22811247 | CM | Complete by 2 Weeks | PC003 | A | CP_ROT102 | FLSH GAS COMPR, GAS COMPR SYS, OKOG1 |  | 2020-01-19 |  | Z1
6 | 11643843 |  | Damaged FGC Drain Hose | NG.AFA.OKOG1.GC | 2018-05-12 | NOCO ORAS | CLSD | 2018-05-12 |  |  | 22660730 | CM | Complete by 6 Months |  | B | NO_MAINT1 | GAS COMPR SYS, OKOG1 |  | 2018-07-02 |  | Z1
2 | 11663363 |  | Liquid ingress into 2nd & 3rd stg FGC | NG.OKOG1.K-5601-K-5601LOD | 2018-08-12 | NOCO ORAS | CLSD | 2018-08-12 | 31000137111 |  | 22682412 | CM | Complete by 1 Week | PC003 | A | CP_ROT102 | COMP, K-5601, GAS COMPR SYS, OKOG1 | NUOVO PIGNONE FLASH GAS COMPRESSOR K-560 | 2018-08-19 |  | Z1
1 | 11725623 | X | P5603B leaking utility fluid | NG.AFA.OKOG1.GC.P-5603B | 2019-06-30 | NOCO ORAS | CLSD | 2019-06-30 |  |  | 22768103 | CM | Immediate Start |  | B | CP_ROT106 | AUX PMP, GAS COMPR SYS, OKOG1 |  | 2019-07-02 |  | Z1
3 | 11650939 | X | Unusual noise from FGC Aux P5602 | NG.AFA.OKOG1.GC.P-5602 | 2018-06-12 | NOCO ORAS | CLSD | 2018-06-12 |  |  | 22667537 | CM | Complete by 2 Weeks |  | B | CP_ROT106 | L/OIL AUX PUMP, GAS COMPR SYS, OKOG1 |  | 2018-06-19 |  | Z1

## WOs
Main work center | Order | Basic start date | ABC indicator | Scheduled finish | Latest Allowed Finish Date | User Status | System status | Description | FunctLocDescrip. | Functional Location | Scheduled start | Original Latest Allowed Finish Date | Actual Finish Date | Order Type | Priority | Equipment | Created on | Basic finish date | Actual start date | Group | Group Counter | Maintenance item | Maintenance Plan | Cost Center | Object Description | Assembly desc. | Execution Condition | Long text exists | Notification | Object list | Priority type | PO Number | System Condition | Total planned costs | Estimated costs | Total actual costs
AFAMECH | 22750164 | 2019-04-02 | B | 2019-04-03 | 2019-04-08 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Cut belt on FGC aftercooler E-5603C | FAN, E-5603, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5603-E-5603FAN | 2019-04-02 | 2019-04-08 | 2019-04-03 | 72FC | 2 | 31000137441 | 2019-04-02 | 2019-04-03 | 2019-04-02 | [5 empty] | MOORE FANS FAN |  | ONTR |  | 11707648 | 815467 | CM |  | 0 | 919.6 | 919.6 | 919.6
AFAMECH | 22868173 | 2020-09-30 | B | 2020-10-01 | 2020-10-03 | XCNF XGI | TECO CNF ESTC NMAT PRC SETC | CUT FAN BELT ON AFTERCOOLER EM-5603C. | FAN, E-5603, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5603-E-5603FAN | 2020-09-30 | 2020-10-03 | 2020-10-05 | 72FC | 4 | 31000137441 | 2020-09-06 | 2020-10-01 | 2020-09-30 | [5 empty] | MOORE FANS FAN |  | ONTR |  | 11807765 | 905537 | CM |  | 0 | 760 | 760 | 760
AFAMECH | 22790514 | 2019-10-28 | B | 2019-10-28 | 2019-10-29 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Cut Fan Belt on E-5603C & D | FAN, E-5603, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5603-E-5603FAN | 2019-10-28 | 2019-10-29 | 2019-10-29 | 72FC | 3 | 31000137441 | 2019-10-17 | 2019-10-28 | 2019-10-28 | [5 empty] | MOORE FANS FAN |  | ONTR | E | 11748365 | 849846 | CM |  | 0 | 762 | 762 | 404.1
AFAMECH | 22854203 | 2020-07-14 | A | 2020-07-14 | 2020-07-25 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Cut fan belt on EM5601B | MOTOR, E-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5601-EM-5601B | 2020-07-14 | 2020-07-25 | 2020-07-14 | 72FC | 4 |  | 2020-07-01 | 2020-07-14 | 2020-07-14 | [7 empty] | ONTR |  | 11794886 | 894139 | CM |  | 0 | 585.2 | 585.2 | 577.6
AFAMECH | 22870373 | 2020-10-08 | B | 2020-10-09 | 2020-11-15 | XCNF XGI | TECO CNF ESTC NMAT PRC SETC | Cut fan belt on FGC EM-5601A cooler fan | FAN, E-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5601-E-5601FAN | 2020-10-08 | 2020-11-15 | 2020-10-08 | 72FC | 5 | 31000137439 | 2020-09-22 | 2020-10-09 | 2020-10-08 | [5 empty] | MOORE FANS FAN |  | ONTR |  | 11810389 | 908025 | CM |  | 0 | 760 | 760 | 722
AFAMECH | 22879290 | 2020-12-01 | B | 2020-12-02 | 2021-05-08 | EXEC | REL CNF ESTC NMAT PRC SETC | Cut fan belt on FGC EM-5602A Cooler Fan | FAN, E-5602, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5602-E-5602FAN | 2020-12-01 | 2021-05-08 | 2020-12-01 | 72FC | 6 | 31000137440 | 2020-11-10 | 2020-12-02 | 2020-12-01 | [5 empty] | MOORE FANS FAN |  | ONTR |  | 11819607 | 915822 | CM |  | 0 | 1216 | 1216 | 1216
AFAMECH | 22870374 | 2020-11-01 | B | 2020-11-01 | 2020-11-16 | XCNF XGI | TECO CNF ESTC NMAT PRC SETC | Cut fan belt on FGC EM-5602B cooler fan | FAN, E-5602, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5602-E-5602FAN | 2020-11-01 | 2020-11-16 | 2020-11-02 | 72FC | 5 | 31000137440 | 2020-09-22 | 2020-11-01 | 2020-10-01 | [5 empty] | MOORE FANS FAN |  | ONTR |  | 11810548 | 908026 | CM |  | 0 | 760 | 760 | 760
AFAELEC | 22688891 | 2018-09-06 | A | 2018-09-06 | 2018-09-12 | XCNF XGI | CLSD CNF PRT NMAT PRC SETC | EM5603B fan belt fall from position | MOTOR, E-5603, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5603-EM-5603B | 2018-09-06 | 2018-09-12 | 2018-09-09 | 72FC | 2 | 31000137095 | 2018-09-08 | 2018-09-06 | 2018-09-06 | [5 empty] | ELECTRIC MOTOR |  | ONTR |  | 11668003 | 774406 | CM |  | 0 | 304 | 304 | 304
AFAMECH | 22763787 | 2019-06-07 | A | 2019-06-07 | 2019-06-14 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Replace Cut belt on FGC Fan E-5601B | MOTOR, E-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5601-EM-5601B | 2019-06-07 | 2019-06-14 | 2019-06-07 | 72FC | 2 |  | 2019-06-07 | 2019-06-07 | 2019-06-07 | [7 empty] | ONTR | E | 11720730 | 826749 | CM |  | 0 | 653.6 | 653.6 | 653.6
AFAMECH | 22769043 | 2019-07-05 | B | 2019-07-05 | 2019-08-02 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Replace Cut fan belt on EM5601A | FAN, E-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5601-E-5601FAN | 2019-07-05 | 2019-08-02 | 2019-07-05 | 72FC | 4 | 31000137439 | 2019-07-05 | 2019-07-05 | 2019-07-05 | [5 empty] | MOORE FANS FAN |  | ONTR |  | 11726689 | 831719 | CM |  | 0 | 805.6 | 805.6 | 805.6
AFAMECH | 22679227 | 2018-08-12 | B | 2018-08-12 | 2018-09-24 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | REPLACE CUT/LOOSE FAN BELT ON E-5605A | FAN, E-5605, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5605-E-5605FAN | 2018-08-12 | 2018-09-24 | 2018-08-12 | 72FC | 5 | 31000137443 | 2018-08-01 | 2018-08-12 | 2018-08-12 | [5 empty] | NUOVO PIGNONE FAN |  | ONTR |  | 11660784 | 767568 | CM |  | 0 | 714.4 | 714.4 | 714.4
AFAMECH | 22688699 | 2018-09-07 | B | 2018-09-08 | 2018-10-04 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Replace Drive Belt on E-5603B | FAN, E-5603, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5603-E-5603FAN | 2018-09-07 | 2018-10-04 | 2018-09-08 | 72FC | 4 | 31000137441 | 2018-09-07 | 2018-09-08 | 2018-09-07 | [5 empty] | MOORE FANS FAN |  | ONTR |  | 11668279 | 774258 | CM |  | 0 | 919.6 | 919.6 | 919.6
AFAMECH | 22858044 | 2020-07-24 | B | 2020-07-25 | 2020-09-09 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Replace Drive Belt on E-5603C | FAN, E-5603, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5603-E-5603FAN | 2020-07-24 | 2020-09-09 | 2020-07-25 | 72FC | 5 | 31000137441 | 2020-07-17 | 2020-07-25 | 2020-07-24 | [5 empty] | MOORE FANS FAN |  | ONTR |  | 11798162 | 896906 | CM |  | 0 | 919.6 | 919.6 | 919.6
AFAMECH | 22871066 | 2020-09-29 | B | 2020-09-30 | 2020-09-30 | XCNF XGI | TECO CNF ESTC NMAT PRC SETC | REPLACE E-5601B AFTER-COOLER FAN BELT | FAN, E-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5601-E-5601FAN | 2020-09-29 | 2020-09-30 | 2020-09-29 | 72FC | 2 | 31000137439 | 2020-09-25 | 2020-09-30 | 2020-09-29 | [5 empty] | MOORE FANS FAN |  | ONTR |  | 11811004 | 908551 | CM |  | 0 | 760 | 760 | 1109.6
AFAMECH | 22756013 | 2019-05-22 | B | 2019-05-23 | 2019-05-25 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Replace E-5603C Snapped Drive Belt | FAN, E-5603, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5603-E-5603FAN | 2019-05-22 | 2019-05-25 | 2019-05-23 | 72FC | 4 | 31000137441 | 2019-04-27 | 2019-05-23 | 2019-05-22 | [5 empty] | MOORE FANS FAN |  | ONTR |  | 11712724 | 819859 | CM |  | 0 | 722 | 722 | 722
AFAMECH | 22699693 | 2018-10-24 | A | 2018-10-24 | 2018-10-26 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | REPLACE CUT FAN BELT ON EM-5601A | STG1 AFTR COOLR, GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC.E-5601 | 2018-10-24 | 2018-10-26 | 2018-10-24 | 72FC | 1 | 31000137057 | 2018-10-24 | 2018-10-24 | 2018-10-24 | [5 empty] | NUOVO PIGNONE STG1 AFTR COOLR | TRANSMISSION BELT,ICF000001996,NU-PI | ONTR |  | 11677073 | 783368 | CM |  | 0 | 638.4 | 638.4 | 638.4
AFAMECH | 22685146 | 2018-08-26 | A | 2018-08-26 | 2018-08-29 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | REPLACE CUT FAN BELT ON E-5601B | STG1 AFTR COOLR, GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC.E-5601 | 2018-08-26 | 2018-08-29 | 2018-08-26 | 72FC | 2 | 31000137057 | 2018-08-23 | 2018-08-26 | 2018-08-26 | [5 empty] | NUOVO PIGNONE STG1 AFTR COOLR | NUOVO PIGNONE STG1 AFTR COOLR | ONTR |  | 11665410 | 771560 | CM |  | 0 | 585.2 | 585.2 | 585.2
AFAMECH | 22873732 | 2020-10-19 | A | 2020-10-19 | 2020-10-25 | XCNF XGI | TECO CNF ESTC NMAT PRC SETC | 2nd stage air cooler fan EM5602B belt cu | STG2 AFTR COOLR, GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC.E-5602 | 2020-10-19 | 2020-10-25 | 2020-10-19 | 72FC | 3 | 31000137058 | 2020-10-12 | 2020-10-19 | 2020-10-19 | [5 empty] | NUOVO PIGNONE STG2 AFTR COOLR | TRANSMISSION BELT,ICF000001902,NU-PI | ONTR | E | 11814232 | 911221 | CM |  | 0 | 380 | 380 | 380
AFAMECH | 22873436 | 2020-10-25 | A | 2020-10-26 | 2020-11-06 | EXEC | REL CNF ESTC NMAT PRC SETC | stage 3 air cooler EM5603D fan belt cut | STG3 AFTR COOLR, GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC.E-5603 | 2020-10-25 | 2020-11-06 | 2020-11-02 | 72FC | 4 | 31000137059 | 2020-10-10 | 2020-10-26 | 2020-10-25 | [5 empty] | NUOVO PIGNONE STG3 AFTR COOLR | TRANSMISSION BELT,ICF000001902,NU-PI | ONTR | E | 11813893 | 910982 | CM |  | 0 | 988 | 608 | 988
AFAMECH | 22873437 | 2020-10-22 | A | 2020-10-22 | 2020-11-06 | XCNF XGI | TECO CNF ESTC NMAT PRC SETC | stage 3 air cooler EM5603C fan belt cut | STG3 AFTR COOLR, GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC.E-5603 | 2020-10-22 | 2020-11-06 | 2020-10-23 | 72FC | 4 | 31000137059 | 2020-10-10 | 2020-10-22 | 2020-10-22 | [5 empty] | NUOVO PIGNONE STG3 AFTR COOLR | TRANSMISSION BELT,ICF000001902,NU-PI | ONTR |  | 11813906 | 910983 | CM |  | 0 | 608 | 608 | 608
AFAMECH | 22868172 | 2020-09-14 | A | 2020-09-14 | 2020-09-17 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Repalce Stg 3 EM5603C Fan Belt | STG3 AFTR COOLR, GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC.E-5603 | 2020-09-14 | 2020-09-17 | 2020-09-14 | 72FC | 3 | 31000137059 | 2020-09-06 | 2020-09-14 | 2020-09-14 | [5 empty] | NUOVO PIGNONE STG3 AFTR COOLR | TRANSMISSION BELT,ICF000001902,NU-PI | ONTR |  | 11807519 | 905535 | CM |  | 0 | 608 | 608 | 577.6
AFAMECH | 22783044 | 2019-09-18 | A | 2019-09-19 | 2019-10-08 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | 3rd stg Air cooler fan EM5603C belt cut | STG3 AFTR COOLR, GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC.E-5603 | 2019-09-18 | 2019-10-08 | 2019-09-18 | 72FC | 4 | 31000137059 | 2019-09-11 | 2019-09-19 | 2019-09-18 | [5 empty] | NUOVO PIGNONE STG3 AFTR COOLR |  | ONTR |  | 11739984 | 843469 | CM |  | 0 | 813.2 | 813.2 | 798
AFAMECH | 22645762 | 2018-03-20 | A | 2018-03-20 | 2018-04-10 | XCNF XGI | CLSD CNF CSER NMAT PRC SETC | Replace Fan belt on E-5603C @ FGC | STG3 AFTR COOLR, GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC.E-5603 | 2018-03-20 | 2018-04-10 | 2018-03-20 | 72FC | 4 | 31000137059 | 2018-03-15 | 2018-03-20 | 2018-03-20 | [5 empty] | NUOVO PIGNONE STG3 AFTR COOLR |  | ONTR | E | 11630527 | 740816 | CM |  | 0 | 0 | 0 | 843.6
AFAMECH | 22847726 | 2020-07-25 | B | 2020-07-26 | 2020-11-26 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Slipped Drive Fan Belt on E-5605B | FAN, E-5605, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5605-E-5605FAN | 2020-07-25 | 2020-11-26 | 2020-07-25 | 72FC | 6 | 31000137443 | 2020-05-31 | 2020-07-26 | 2020-07-25 | [5 empty] | NUOVO PIGNONE FAN |  | ONTR |  | 11789907 | 888931 | CM |  | 0 | 851.2 | 851.2 | 843.6
AFAMECH | 22784203 | 2019-09-23 | B | 2019-09-24 | 2019-10-14 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | 4th Stg discharge cooler fan A belt cut | FAN, E-5604, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5604-E-5604FAN | 2019-09-23 | 2019-10-14 | 2019-09-24 | 72FC | 4 | 31000137442 | 2019-09-17 | 2019-09-24 | 2019-09-23 | [5 empty] | MOORE FANS FAN |  | ONTR |  | 11741620 | 844594 | CM |  | 0 | 813.2 | 813.2 | 813.2
AFAMECH | 22698275 | 2018-11-30 | A | 2018-11-30 | 2018-12-11 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Replace pulled out belt on EM-5601B. | MOTOR, E-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5601-EM-5601B | 2018-11-30 | 2018-12-11 | 2018-11-30 | 72FC | 5 |  | 2018-10-18 | 2018-11-30 | 2018-11-30 | [7 empty] | ONTR |  | 11675630 | 781786 | CM |  | 0 | 456 | 456 | 380
AFAMECH | 22740093 | 2019-02-11 | B | 2019-02-11 | 2019-04-03 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Replace Worn Drive Belt on E-5601B | FAN, E-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5601-E-5601FAN | 2019-02-11 | 2019-04-03 | 2019-02-11 | 72FC | 5 | 31000137439 | 2019-02-07 | 2019-02-11 | 2019-02-11 | [5 empty] | MOORE FANS FAN |  | ONTR |  | 11697903 | 805921 | CM |  | 0 | 676.4 | 676.4 | 676.4
AFAMECH | 22677667 | 2018-08-20 | B | 2018-08-20 | 2019-01-19 | XCNF XGI | CLSD CNF ESTC CSER NMAT PRC SETC | FGC Cooler Fan E-5603A Belt Alignment | FAN, E-5603, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5603-E-5603FAN | 2018-08-20 | 2019-01-19 | 2018-08-20 | 72FC | 6 | 31000137441 | 2018-07-25 | 2018-08-20 | 2018-08-20 | [5 empty] | MOORE FANS FAN |  | ONTR |  | 11659528 | 766283 | CM |  | 0 | 577.6 | 554.8 | 577.6
AFAMECH | 22676901 | 2018-07-26 | B | 2018-07-26 | 2018-07-29 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Replace Belt on 1st Stage fan E-5601A | FAN, E-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5601-E-5601FAN | 2018-07-26 | 2018-07-29 | 2018-07-26 | 72FC | 2 | 31000137439 | 2018-07-22 | 2018-07-26 | 2018-07-26 | [5 empty] | MOORE FANS FAN |  | ONTR |  | 11659347 | 765865 | CM |  | 0 | 790.4 | 790.4 | 790.4
AFAMECH | 22873959 | 2020-10-21 | A | 2020-10-22 | 2020-10-27 | XCNF XGI | TECO CNF ESTC NMAT PRC SETC | 1st stge air cooler fan EM5601B belt cut | STG1 AFTR COOLR, GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC.E-5601 | 2020-10-21 | 2020-10-27 | 2020-10-21 | 72FC | 3 | 31000137057 | 2020-10-13 | 2020-10-22 | 2020-10-21 | [5 empty] | NUOVO PIGNONE STG1 AFTR COOLR | TRANSMISSION BELT,ICF000001996,NU-PI | ONTR |  | 11814546 | 911372 | CM |  | 0 | 912 | 304 | 684
AFAELEC | 22644257 | 2018-04-23 | A | 2018-04-23 | 2018-09-04 | XCNF XGI | CLSD CNF NMAT PRC SETC | Troubleshoot the cause of unusual noise | MOTOR, E-5603, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5603-EM-5603A | 2018-04-23 | 2018-09-04 | 2018-04-23 | 72FC | 6 | 31000137094 | 2018-03-10 | 2018-04-23 | 2018-04-23 | [5 empty] | ELECTRIC MOTOR |  | ONTR | E | 11629379 | 739676 | CM |  | 0 | 912 | 0 | 912
AFAELEC | 22688890 | 2018-09-19 | A | 2018-09-19 | 2018-10-03 | XCNF XGI | CLSD CNF PRT NMAT PRC SETC | Unusual noise from EM5603A | MOTOR, E-5603, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5603-EM-5603A | 2018-09-19 | 2018-10-03 | 2018-09-19 | 72FC | 4 | 31000137094 | 2018-09-08 | 2018-09-19 | 2018-09-19 | [5 empty] | ELECTRIC MOTOR |  | ONTR |  | 11668012 | 774400 | CM |  | 0 | 304 | 304 | 304
AFAMECH | 22885005 | 2020-12-07 | A | 2020-12-08 | 2020-12-08 | XCNF XGI | TECO CNF GMPS NMAT PRC SETC | Unusual noise on 3rd stage fan EM5603A | MOTOR, E-5603, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5603-EM-5603A | 2020-12-07 | 2020-12-08 | 2020-12-09 | 72FC | 2 | 31000137095 | 2020-12-07 | 2020-12-08 | 2020-12-07 | [5 empty] | ELECTRIC MOTOR | BALL BEARING,6-026892-08-83/56,EBARA | ONTR | E | 11823870 | 921516 | CM |  | 0 | 1495.1 | 963.1 | 1495.1
AFAMECH | 22823059 | 2020-07-25 | B | 2020-07-26 | 2021-02-07 | XCNF XGI | CLSD CNF ESTC GMPS NMAT PRC SETC | Wobbling Fan Block/Pulley on E-5601A | FAN, E-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5601-E-5601FAN | 2020-07-25 | 2021-02-07 | 2020-07-25 | 72FC | 7 | 31000137439 | 2020-02-18 | 2020-07-26 | 2020-07-25 | [5 empty] | MOORE FANS FAN |  | ONTR |  | 11771754 | 872202 | CM |  | 0 | 4324.46 | 4324.46 | 4324.45
AFAMECH | 22874435 | 2020-10-27 | A | 2020-10-27 | 2020-11-10 | XCNF XGI | TECO CNF ESTC NMAT PRC SETC | 1st stag coolr fan EM5601A unusual noise | STG1 AFTR COOLR, GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC.E-5601 | 2020-10-27 | 2020-11-10 | 2020-10-27 | 72FC | 4 | 31000137057 | 2020-10-15 | 2020-10-27 | 2020-10-27 | [5 empty] | NUOVO PIGNONE STG1 AFTR COOLR | TRANSMISSION BELT,ICF000001996,NU-PI | ONTR |  | 11814667 | 911634 | CM |  | 0 | 456 | 456 | 456
AFAMECH | 22872415 | 2020-10-12 | A | 2020-10-12 | 2020-11-01 | XCNF XGI | TECO CNF ESTC NMAT PRC SETC | 1st stag coolr fan EM5601B unusual noise | STG1 AFTR COOLR, GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC.E-5601 | 2020-10-12 | 2020-11-01 | 2020-10-12 | 72FC | 4 | 31000137057 | 2020-10-05 | 2020-10-12 | 2020-10-12 | [5 empty] | NUOVO PIGNONE STG1 AFTR COOLR |  | ONTR |  | 11813047 | 909974 | CM |  | 0 | 608 | 608 | 608
AFAELEC | 22666756 | 2018-08-30 | A | 2018-08-30 | 2018-08-31 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Rectify the Unusual noice on 2nd Stage a | MOTOR, E-5602, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5602-EM-5602A | 2018-08-30 | 2018-07-04 | 2018-08-30 | 72FC | 4 | 31000137089 | 2018-06-10 | 2018-08-30 | 2018-08-30 | [5 empty] | ELECTRIC MOTOR |  | ONTR | E | 11649888 | 757919 | CM |  | 0 | 912 | 912 | 912
AFAMECH | 22868177 | 2020-09-26 | A | 2020-09-26 | 2021-02-28 | XCNF XGI | TECO CNF ESTC NMAT PRC SETC | Resolve FGC unusual noise from stage 4 | FLSH GAS COMPR, GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC.K-5601 | 2020-09-26 | 2021-02-28 | 2020-09-26 | 72FC | 6 |  | 2020-09-06 | 2020-09-26 | 2020-09-26 | [7 empty] | ONTR |  | 11807021 | 905541 | CM |  | 0 | 782.8 | 782.8 | 934.8
AFAINST | 22787600 | 2019-10-18 | A | 2019-10-18 | 2019-11-28 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | EM5601A not starting on Auto | MOTOR, E-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5601-EM-5601A | 2019-10-18 | 2019-11-28 | 2019-10-18 | 72FC | 5 | 31000137086 | 2019-10-04 | 2019-10-18 | 2019-10-18 | [5 empty] | ELECTRIC MOTOR |  | ONTR |  | 11745570 | 847469 | CM |  | 0 | 231 | 231 | 231
AFAINST | 22787601 | 2019-10-20 | A | 2019-10-20 | 2019-11-28 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | EM5602A not starting on Auto | MOTOR, E-5602, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5602-EM-5602A | 2019-10-20 | 2019-11-28 | 2019-10-21 | 72FC | 5 | 31000137089 | 2019-10-04 | 2019-10-20 | 2019-10-20 | [5 empty] | ELECTRIC MOTOR |  | ONTR |  | 11745571 | 847470 | CM |  | 0 | 231 | 231 | 231
AFAINST | 22787603 | 2019-10-20 | A | 2019-10-20 | 2019-11-28 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | EM5603A not starting on Auto | MOTOR, E-5603, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5603-EM-5603A | 2019-10-20 | 2019-11-28 | 2019-10-21 | 72FC | 5 | 31000137095 | 2019-10-04 | 2019-10-20 | 2019-10-20 | [5 empty] | ELECTRIC MOTOR |  | ONTR |  | 11745572 | 847472 | CM |  | 0 | 231 | 231 | 231
AFAINST | 22787602 | 2019-11-25 | A | 2019-11-25 | 2019-11-28 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | EM5603B failed on demand/Auto | MOTOR, E-5603, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5603-EM-5603B | 2019-11-25 | 2019-11-28 | 2019-11-25 | 72FC | 5 | 31000137094 | 2019-10-04 | 2019-11-25 | 2019-11-25 | [5 empty] | ELECTRIC MOTOR |  | ONTR |  | 11745574 | 847471 | CM |  | 0 | 231 | 231 | 231
AFAINST | 22787604 | 2019-11-25 | A | 2019-11-25 | 2019-11-28 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | EM5604A failed on demand/Auto | MOTOR, E-5604, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5604-EM-5604A | 2019-11-25 | 2019-11-28 | 2019-11-25 | 72FC | 5 | 31000137099 | 2019-10-04 | 2019-11-25 | 2019-11-25 | [5 empty] | ELECTRIC MOTOR |  | ONTR |  | 11745578 | 847473 | CM |  | 0 | 231 | 231 | 231
AFAELEC | 22843566 | 2020-07-01 | A | 2020-07-01 | 2020-11-07 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | EM5604A not running on manual | MOTOR, E-5604, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5604-EM-5604A | 2020-07-01 | 2020-11-07 | 2020-07-01 | 72FC | 6 | 31000137099 | 2020-05-12 | 2020-07-01 | 2020-07-01 | [5 empty] | ELECTRIC MOTOR |  | ONTR |  | 11786418 | 885707 | CM |  | 0 | 380 | 380 | 380
AFAELEC | 22784946 | 2019-10-11 | B | 2019-10-11 | 2019-11-14 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | FGC 4th stage fan B not starting on Auto | RCU, E-5604, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5604-RCUEM5604B | 2019-10-11 | 2019-11-14 | 2019-10-11 | 72FC | 5 |  | 2019-09-21 | 2019-10-11 | 2019-10-11 | [7 empty] | ONTR |  | 11742656 | 845258 | CM |  | 0 | 616 | 616 | 308
AFAELEC | 22759724 | 2019-05-12 | A | 2019-05-13 | 2019-05-14 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | FGC EM5606B trips on overload | MOTOR, E-5606, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5606-EM-5606B | 2019-05-12 | 2019-05-14 | 2019-06-08 | 72FC | 1 | 31000137104 | 2019-05-13 | 2019-05-13 | 2019-05-12 | [5 empty] | ELECTRIC MOTOR |  | ONTR |  | 11715823 | 822573 | CM |  | 0 | 608 | 608 | 608
AFAELEC | 22651767 | 2018-06-06 | A | 2018-06-06 | 2018-10-04 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Troubleshoot & repair incessant tripping | MOTOR, E-5603, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5603-EM-5603B | 2018-06-06 | 2018-10-04 | 2018-06-06 | 72FC | 6 | 31000137095 | 2018-04-08 | 2018-06-06 | 2018-04-14 | [5 empty] | ELECTRIC MOTOR |  | ONTR | E | 11635781 | 745202 | CM |  | 0 | 3040 | 3040 | 3040
AFAELEC | 22653045 | 2018-07-30 | A | 2018-07-30 | 2018-07-30 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | TROUBLESHOOT & REPAIR TRIPPING FAULT ON | MOTOR, E-5603, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5603-EM-5603A | 2018-07-30 | 2018-04-26 | 2018-07-30 | 72FC | 3 | 31000137094 | 2018-04-13 | 2018-07-30 | 2018-04-14 | [5 empty] | ELECTRIC MOTOR |  | ONTR | E | 11637074 | 746324 | CM |  | 0 | 3040 | 3040 | 2888
AFAELEC | 22674191 | 2018-11-06 | A | 2018-11-06 |  | XCNF XGI | CLSD CNF ESTC GMPS NMAT PRC SETC | CHECK AND REPAIR EM-5601B - 1st Stg Aft | MOTOR, E-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5601-EM-5601B | 2018-11-06 |  | 2018-10-02 | 72RE | 3 |  | 2018-07-11 | 2019-02-04 | 2018-10-02 | [8 empty] | E | 11673028 | 778598 | GM |  |  | 1791.87 | 1791.87 | 1790.66
MT7ELEC | 22756315 | 2019-05-20 | A | 2019-05-20 |  | APPR | REL ESTC GMPS NMAT PRC SETC | Check, plan & repair faulty EM-5602A EX | MOTOR, E-5602, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5602-EM-5602A | 2019-05-20 |  |  | 72RE | 3 | 31000137089 | 2019-04-29 | 2019-07-28 | [6 empty] | ELECTRIC MOTOR |  |  | E |  | 0 | GM |  |  | 1809.51 | 1809.51 | 1809.38
AFAELEC | 22663329 | 2018-05-31 | A | 2018-05-31 | 2018-06-01 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Disconnect and Pull out Electric Motor-E | MOTOR, E-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5601-EM-5601B | 2018-05-31 | 2018-06-01 | 2018-05-31 | 72FC | 2 |  | 2018-05-26 | 2018-05-31 | 2018-05-31 | [7 empty] | ONTR | E | 11646788 | 754826 | CM |  | 0 | 912 | 912 | 912
MT7ELEC | 22670840 | 2018-06-28 | A | 2018-06-28 |  | XCNF XGI | CLSD CNF NMAT PRC SETC | EL-2214 INSPECT AND REPAIR ELECTRIC MOTO | MOTOR, E-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5601-EM-5601A | 2018-06-28 |  | 2018-07-24 | 72RE | 1 | 31000137086 | 2018-06-28 | 2018-07-08 | 2018-06-28 | [5 empty] | ELECTRIC MOTOR |  |  | E |  | 0 | GM |  |  | 1064 | 1064 | 1064
AFAELEC | 22887641 | 2020-12-25 | B | 2020-12-25 | 2021-06-15 | XCNF XGI | TECO CNF ESTC NMAT PRC SETC | Defective cooler fan motor EM-5101C | FAN, E-5101C, COND TRANS SYS, OKOG1 | NG.OKOG1.E-5101C-E-5101CFAN | 2020-12-25 | 2021-06-15 | 2020-12-25 | 72FC | 6 | 31000137435 | 2020-12-18 | 2020-12-25 | 2020-12-25 | [5 empty] | FLOWSERVE 65 WUC-2R-23 FAN |  | ONTR |  | 11827013 | 923891 | CM |  | 0 | 608 | 608 | 608
AFAELEC | 22764126 | 2019-07-15 | A | 2019-07-15 | 2019-12-04 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | FGC 1st Stage EM-5601A failed on demand | MOTOR, E-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5601-EM-5601A | 2019-07-15 | 2019-12-04 | 2019-07-15 | 72FC | 6 | 31000137086 | 2019-06-08 | 2019-07-15 | 2019-07-15 | [5 empty] | ELECTRIC MOTOR | ELECTRIC MOTOR | ONTR | E | 11720758 | 826912 | CM |  | 0 | 608 | 608 | 608
AFAMECH | 22677665 | 2018-08-04 | B | 2018-08-05 | 2018-08-06 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | FGC Cooler Fan E-5601A Repairs | FAN, E-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5601-E-5601FAN | 2018-08-04 | 2018-08-06 | 2018-08-05 | 72FC | 3 | 31000137439 | 2018-07-25 | 2018-08-05 | 2018-08-04 | [5 empty] | MOORE FANS FAN |  | ONTR |  | 11659520 | 766281 | CM |  | 0 | 4871.6 | 4871.6 | 4871.6
AFAMECH | 22677666 | 2018-12-02 | B | 2018-12-02 | 2019-01-19 | XCNF XGI | CLSD CNF NMAT PRC SETC | FGC Cooler Fan E-5602A suspected faulty | FAN, E-5602, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5602-E-5602FAN | 2018-12-02 | 2019-01-19 | 2018-12-02 | 72FC | 6 | 31000137440 | 2018-07-25 | 2018-12-02 | 2018-12-02 | [5 empty] | MOORE FANS FAN |  | ONTR |  | 11659524 | 766282 | CM |  | 0 | 304 | 304 | 304
AFAELEC | 22630423 | 2018-03-29 | A | 2018-03-29 | 2018-04-30 | XCNF XGI | CLSD CNF PRT NMAT PRC SETC | Install and terminate EM-5606B Tempered | MOTOR, E-5606, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5606-EM-5606B | 2018-03-29 | 2018-01-27 | 2018-03-29 | 72FC | 3 | 31000137104 | 2018-01-14 | 2018-03-29 | 2018-03-29 | [5 empty] | ELECTRIC MOTOR |  | ONTR | E | 11617292 | 728658 | CM |  | 0 | 1216 | 0 | 1216
AFAELEC | 22654171 | 2018-06-04 | A | 2018-06-04 | 2018-07-31 | XCNF XGI | CLSD CNF NMAT PRC SETC | Install Electric Motor EM-5602A- 2nd Sta | MOTOR, E-5602, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5602-EM-5602A | 2018-06-04 | 2018-05-01 | 2018-06-04 | 72FC | 3 | 31000137089 | 2018-04-19 | 2018-06-04 | 2018-04-21 | [5 empty] | ELECTRIC MOTOR |  | ONTR | E | 11638113 | 747372 | CM |  | 0 | 1824 | 0 | 1824
AFAELEC | 22658797 | 2018-06-08 | A | 2018-06-08 | 2018-06-28 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Troubleshoot & Repair the cause of EM-56 | MOTOR, E-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5601-EM-5601A | 2018-06-08 | 2018-06-28 | 2018-06-08 | 72FC | 5 | 31000137086 | 2018-05-06 | 2018-06-08 | 2018-06-08 | [5 empty] | ELECTRIC MOTOR |  | ONTR | E | 11641573 | 750585 | CM |  | 0 | 608 | 1368 | 608
AFAELEC | 22714153 | 2019-06-13 | A | 2019-06-13 | 2019-06-19 | XCNF XGI | CLSD CNF NMAT PRC SETC | Troubleshoot fault on FGC 4th Stg EM-560 | MOTOR, E-5604, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5604-EM-5604A | 2019-06-13 | 2019-06-19 | 2019-06-13 | 72FC | 6 | 31000137099 | 2018-12-22 | 2019-06-13 | 2019-06-13 | [5 empty] | ELECTRIC MOTOR |  | ONTR | E | 11688584 | 794444 | CM |  | 0 | 912 | 0 | 912
AFAELEC | 22686251 | 2018-10-13 | A | 2018-10-13 | 2018-10-22 | XCNF XGI | CLSD CNF PRT NMAT PRC SETC | Troubleshoot FGC 4th Stg EM-5604A trips. | MOTOR, E-5604, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5604-EM-5604A | 2018-10-13 | 2018-10-22 | 2018-10-13 | 72FC | 5 | 31000137099 | 2018-08-28 | 2018-10-13 | 2018-10-13 | [5 empty] | ELECTRIC MOTOR |  | ONTR |  | 11666144 | 772246 | CM |  | 0 | 988 | 988 | 912
AFAMECH | 22656068 | 2018-05-07 | C | 2018-05-07 | 2018-05-23 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Cleaning of Lube oil Filter F-5601A | L/OIL FLTR A, GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC.F-5601A | 2018-05-07 | 2018-05-23 | 2018-05-07 | 72FC | 4 | 31000137446 | 2018-04-27 | 2018-05-07 | 2018-05-07 | [5 empty] | FILTERSD6PW43F30F01/RC026039L/OIL FLTR |  | ONTR | E | 11639747 | 748701 | CM |  | 0 | 691.6 | 691.6 | 691.6
AFAMECH | 22656070 | 2018-05-07 | C | 2018-05-07 | 2018-05-23 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Cleaning of Lube oil Filter F-5601B | L/OIL FLTR B, GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC.F-5601B | 2018-05-07 | 2018-05-23 | 2018-05-07 | 72FC | 4 | 31000137447 | 2018-04-27 | 2018-05-07 | 2018-05-07 | [5 empty] | FILTERS L/OIL FLTR B |  | ONTR | E | 11639744 | 748803 | CM |  | 0 | 744.8 | 744.8 | 744.8
AFAMECH | 22678386 | 2018-08-05 | C | 2018-08-05 | 2018-08-10 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | REPLACE FGC LUBE OIL FILTER F-5601A | L/OIL FLTR A, GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC.F-5601A | 2018-08-05 | 2018-08-10 | 2018-08-05 | 72FC | 3 | 31000137446 | 2018-07-28 | 2018-08-05 | 2018-08-05 | [5 empty] | FILTERSD6PW43F30F01/RC026039L/OIL FLTR |  | ONTR |  | 11660276 | 766915 | CM |  | 0 | 866.4 | 866.4 | 866.4
AFAMECH | 22678387 | 2018-08-02 | C | 2018-08-02 | 2018-08-10 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | REPLACE FGC LUBE OIL FILTER F-5601B | L/OIL FLTR B, GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC.F-5601B | 2018-08-02 | 2018-08-10 | 2018-08-04 | 72FC | 3 | 31000137447 | 2018-07-28 | 2018-08-02 | 2018-08-02 | [5 empty] | FILTERS L/OIL FLTR B |  | ONTR |  | 11660277 | 766916 | CM |  | 0 | 866.4 | 866.4 | 1474.4
AFAMECH | 22773428 | 2019-08-07 | A | 2019-08-07 | 2019-08-08 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Rectify FGC 3rd stg Strainer line leak | STG 3 S/SCRUB, GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC.V-5603 | 2019-08-07 | 2019-08-02 | 2019-08-08 | 72FC | 2 | 31000137347 | 2019-07-27 | 2019-08-07 | 2019-08-07 | [5 empty] | CMS SRL STG 3 S/SCRUB |  | SDTA |  | 11730797 | 835470 | CM |  | 0 | 1216 | 1216 | 1216
AFAMECH | 22689536 | 2018-09-24 | B | 2019-04-18 |  | APPR | REL PRT CSER GMPS NMAT PRC SETC | Repair of E-5605B Hub | FAN, E-5605, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5605-E-5605FAN | 2019-04-18 |  |  | 72RE | 2 | 31000137443 | 2018-09-11 | [7 empty] | NUOVO PIGNONE FAN |  |  | E |  | 0 | GM |  |  | 759.53 | 759.53 | 759.53
AFAMECH | 22703044 | 2019-02-14 | B | 2019-02-19 |  | APPR | REL GMPS NMAT PRC SETC | FGC Aftercoolers Pillow Block Overhaul | GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC | 2019-02-19 |  |  | 72RE | 2 |  | 2018-11-05 | 2019-02-25 | [11 empty] | 0 | GM |  |  | 17369.75 | 15270.94 | 17367.71
AFAMECH | 22697811 | 2019-04-01 | B | 2019-12-19 |  | APPR | REL ESTC GMPS NMAT PRC SETC | 4 units Fan block assembly Ovehaul | FAN, E-5605, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5605-E-5605FAN | 2019-12-19 |  |  | 72RE |  | 31000137443 | 2018-10-16 | 2019-04-26 | [6 empty] | NUOVO PIGNONE FAN |  |  |  |  | 0 | GM |  |  | 17367.57 | 17368.88 | 17367.63
AFAMECH | 22698805 | 2018-12-03 | B | 2018-12-03 | 2018-12-12 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Rectify High vibration on E-5603B Assemb | FAN, E-5603, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5603-E-5603FAN | 2018-12-03 | 2018-12-12 | 2018-12-04 | 72FC | 5 | 31000137441 | 2018-10-20 | 2018-12-03 | 2018-12-01 | [5 empty] | MOORE FANS FAN |  | ONTR |  | 11675841 | 781971 | CM |  | 0 | 304 | 304 | 304
AFAELEC | 22693218 | 2018-10-17 | A | 2018-10-19 | 2018-10-19 | XCNF XGI | CLSD CNF PRT NMAT PRC SETC | Rectify High vibration on EM-5603B UNIT | MOTOR, E-5603, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5603-EM-5603B | 2018-10-17 | 2018-10-19 | 2018-10-17 | 72FC | 4 | 31000137095 | 2018-09-27 | 2018-10-19 | 2018-10-17 | [5 empty] | ELECTRIC MOTOR |  | ONTR |  | 11670857 | 777700 | CM |  | 0 | 7265.6 | 7265.6 | 7265.6
AFAMECH | 22695401 | 2018-10-05 | A | 2018-10-07 | 2018-10-11 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Rectify FGC Tripping on HH Temp 3rd Stag | COMP, K-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.K-5601-K-5601LOD | 2018-10-05 | 2018-10-11 | 2018-10-07 | 72FC | 2 | 31000137111 | 2018-10-06 | 2018-10-07 | 2018-10-05 | [5 empty] | NUOVO PIGNONE FLASH GAS COMPRESSOR K-560 |  | ONTR | E | 11673457 | 779412 | CM |  | 0 | 3648 | 3648 | 3648
AFAMECH | 22756581 | 2019-05-20 | A | 2019-05-21 | 2019-10-26 | XCNF XGI | CLSD CNF PRT NMAT PRC SETC | Rectify Hi Temp. on FGC 3rd Stg Valves | COMP, K-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.K-5601-K-5601LOD | 2019-05-20 | 2019-10-26 | 2019-05-21 | 72FC | 6 | 31000137111 | 2019-04-30 | 2019-05-21 | 2019-05-20 | [5 empty] | NUOVO PIGNONE FLASH GAS COMPRESSOR K-560 |  | ONTR |  | 11713469 | 820557 | CM |  | 0 | 1953.2 | 1953.2 | 1801.2
AFAMECH | 22674903 | 2018-07-14 | A | 2018-07-15 | 2018-07-20 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Rectify Trip on HH Temp 3rd Stage | COMP, K-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.K-5601-K-5601LOD | 2018-07-14 | 2018-07-20 | 2018-07-15 | 72FC | 2 | 31000137111 | 2018-07-14 | 2018-07-15 | 2018-07-14 | [5 empty] | NUOVO PIGNONE FLASH GAS COMPRESSOR K-560 |  | ONTR |  | 11657620 | 764226 | CM |  | 0 | 2508 | 2508 | 2508
AFAMECH | 22826997 | 2020-03-04 | B | 2020-03-06 | 2020-04-27 | XCNF XGI | TECO CNF ESTC CSER NMAT PRC SETC | High temp on 4th stage suction valve | TE, K-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.K-5601-56TE604B | 2020-03-04 | 2020-04-27 | 2020-03-06 | 72FC | 5 |  | 2020-03-03 | 2020-03-06 | 2020-03-04 | [7 empty] | ONTR |  | 11775535 | 875461 | CM |  | 0 | 608 | 2508 | 608
AFAINST | 22782550 | 2019-09-22 | B | 2019-09-22 | 2019-10-06 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Replace faulty HMI CPU fan | F/GAS COMP C/PANLCP-5601, GAS COMPSYS, O | NG.AFA.OKOG1.GC.CP-5601 | 2019-09-22 | 2019-10-06 | 2019-09-22 | 72FC | 4 | 31000136996 | 2019-09-09 | 2019-09-22 | 2019-09-22 | [5 empty] | F/GAS COMPR CONTROL PANEL |  | ONTR | E | 11739540 | 843141 | CM |  | 0 | 760 | 760 | 760
AFAINST | 22781962 | 2019-09-18 | A | 2019-09-18 | 2019-10-30 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Troubleshoot & restore frozen FGC HMI | FLSH GAS COMPR, GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC.K-5601 | 2019-09-18 | 2019-10-30 | 2019-09-18 | 72FC | 5 |  | 2019-09-06 | 2019-09-18 | 2019-09-18 | [7 empty] | ONTR | E | 11738880 | 842722 | CM |  | 0 | 1064 | 1064 | 1064
AFAINST | 22776184 | 2019-08-31 | C | 2019-08-31 | 2019-10-03 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Rectify Rod-drop Data Streaming Fault, S | POS TRANS, K-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.K-5601-56ZT634 | 2019-08-31 | 2019-10-03 | 2019-08-31 | 72FC | 5 |  | 2019-08-09 | 2019-08-31 | 2019-08-31 | [7 empty] | ONTR | E | 11733349 | 837805 | CM |  | 0 | 760 | 760 | 760
AFAINST | 22873147 | 2020-11-22 | B | 2020-11-22 | 2020-12-03 | EXEC | REL CNF GMPS NMAT PRC SETC | Rectify FGC SIS trip settings default to | GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC | 2020-11-22 | 2020-12-03 | 2020-11-22 | 72FC | 5 |  | 2020-10-08 | 2020-11-22 | 2020-11-22 | [7 empty] | ONTR | E | 11813750 | 910617 | CM |  | 0 | 24956 | 24956 | 4837.59
AFAELEC | 22759766 | 2019-05-21 | A | 2019-05-21 | 2019-05-26 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | EM5606A fail to start CFA feedback error | MOTOR, E-5606, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5606-EM-5606A | 2019-05-21 | 2019-05-26 | 2019-05-21 | 72FC | 3 | 31000137103 | 2019-05-13 | 2019-05-21 | 2019-05-21 | [5 empty] | ELECTRIC MOTOR |  | ONTR |  | 11715822 | 822755 | CM |  | 0 | 456 | 456 | 456
AFAMECH | 22674519 | 2018-08-13 | A | 2018-08-13 |  | APPR | REL GMPS NMAT PRC SETC | Rectify Hi DP alarm on 56PDI130-Manpower | COMP, K-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.K-5601-K-5601LOD | 2018-08-13 |  |  | 72RE | 2 | 31000137111 | 2018-07-13 | [7 empty] | NUOVO PIGNONE FLASH GAS COMPRESSOR K-560 |  |  |  |  | 0 | GM |  |  | 4890.38 | 4890.38 | 4890.38
AFAMECH | 22667537 | 2018-06-19 | B | 2018-06-19 | 2018-06-26 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Rectify unusual noise from FGC Aux P5602 | L/OIL AUX PUMP, GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC.P-5602 | 2018-06-19 | 2018-06-26 | 2018-06-19 | 72FC | 3 |  | 2018-06-14 | 2018-06-19 | 2018-06-19 | [7 empty] | ONTR |  | 11650939 | 758702 | CM |  | 0 | 1307.2 | 1307.2 | 1178
AFAMECH | 22758588 | 2020-02-25 | B | 2020-02-26 | 2020-03-31 | XCNF MAGN MANX XGI | TECO CNF ESTC CSER GMPS PRC SETC | Rectify leaks on FGC Pump P-5603A | PMP, P-5603A, GAS COMPR SYS, OKOG1 | NG.OKOG1.P-5603A-P-5603ALOD | 2020-02-25 | 2019-06-03 | 2020-02-26 | 72FC | 4 | 31000137141 | 2019-05-07 | 2020-02-26 | 2020-02-25 | [5 empty] | NUOVO PIGNONE NT 32-200/01/196-W1 PUMP |  | ONTR |  | 11714719 | 821718 | CM |  | 0 | 10494.57 | 1535.24 | 1992.05
AFAMECH | 22768103 | 2019-07-02 | B | 2019-07-02 | 2019-07-02 | XCNF XGI | CLSD CNF ESTC NMAT PRC SETC | Rectify P5603B leaking utility fluid | AUX PMP, GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC.P-5603B | 2019-07-02 | 2019-07-02 | 2019-07-02 | 72FC | 1 |  | 2019-07-01 | 2019-07-02 | 2019-07-02 | [7 empty] | ONTR |  | 11725623 | 831027 | CM |  | 0 | 889.2 | 889.2 | 889.2
AFAMECH | 22682412 | 2018-08-13 | A | 2018-08-18 | 2018-08-19 | XCNF XGI | CLSD CNF NMAT PRC SETC | Rectify liquid ingress into FGC | COMP, K-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.K-5601-K-5601LOD | 2018-08-13 | 2018-08-19 | 2018-08-18 | 72FC | 2 | 31000137111 | 2018-08-12 | 2018-08-18 | 2018-08-13 | [5 empty] | NUOVO PIGNONE FLASH GAS COMPRESSOR K-560 |  | ONTR | E | 11663363 | 769725 | CM |  | 0 | 4256 | 4256 | 4256
MT5AGG | 22681148 | 2018-08-07 | A | 2018-09-26 |  | APPR | REL GMPS NMAT PRC SETC | RECTIFY SLUDGE INGRESS IN FGC K-5601 | COMP, K-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.K-5601-K-5601LOD | 2018-09-26 |  |  | 72RE |  | 31000137111 | 2018-08-07 | [7 empty] | NUOVO PIGNONE FLASH GAS COMPRESSOR K-560 |  |  |  |  | 0 | GM |  |  | 23041.99 | 13786.92 | 23041.98
MT7ELEC | 22695805 | 2018-10-08 | B | 2018-10-24 |  | APPR | REL ESTC GMPS NMAT PRC SETC | Repair of faulty FGC Aftercooler fan Ele | GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC | 2018-10-24 |  |  | 72RE | 2 |  | 2018-10-08 | 2018-10-22 | [9 empty] | E |  | 0 | GM |  |  | 3682.15 | 2945.95 | 2603.47
AFAMECH | 22425854 | 2019-12-30 | A | 2019-12-30 |  | APPR MANX | REL GMPS PRC SETC | 8000HRS INSPECTION OF FGC K-5601 | COMP, K-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.K-5601-K-5601LOD | 2019-12-30 |  |  | 72RE | 3 | 31000137111 | 2016-02-25 | [7 empty] | NUOVO PIGNONE FLASH GAS COMPRESSOR K-560 |  |  | E |  | 0 | GM |  |  | 432981.84 | 400718.35 | 418703.39
MT7INST | 22807439 | 2019-12-27 | A | 2019-12-27 |  | APPR | REL ESTC CSER GMPS NMAT PRC SETC | Funct Test 4pcs unloader actuator/ machi | COMP, K-5601, GAS COMPR SYS, OKOG1 | NG.OKOG1.K-5601-K-5601LOD | 2019-12-27 |  |  | 72RE | 2 | 31000137111 | 2019-12-25 | [7 empty] | NUOVO PIGNONE FLASH GAS COMPRESSOR K-560 |  |  | E |  | 0 | GM |  |  | 326.82 | 326.82 | 326.82
AFAMECH | 22660730 | 2018-07-02 | B | 2018-07-02 | 2018-11-08 | XCNF XGI | CLSD CNF ESTC GMPS NMAT PRC SETC | INSPECTION OF FLEXIBLE HOSE | GAS COMPR SYS, OKOG1 | NG.AFA.OKOG1.GC | 2018-07-02 | 2018-11-08 | 2018-07-02 | 72FC | 6 |  | 2018-05-14 | 2018-07-02 | 2018-07-02 | [7 empty] | ONTR | E | 11643843 | 752388 | CM |  | 0 | 3337.91 | 4021.99 | 3339.53
AFAELEC | 22644258 | 2018-05-02 | A | 2018-05-02 | 2018-07-31 | XCNF XGI | CLSD CNF NMAT PRC SETC | INSTALL AND COMMISSION BACK EM-5606A | MOTOR, E-5606, GAS COMPR SYS, OKOG1 | NG.OKOG1.E-5606-EM-5606A | 2018-05-02 | 2018-03-22 | 2018-05-02 | 72FC | 3 | 31000137103 | 2018-03-10 | 2018-05-02 | 2018-05-02 | [5 empty] | ELECTRIC MOTOR |  | ONTR | E | 11629380 | 739677 | CM |  | 0 | 1368 | 0 | 1368