## Slide 1: Causal Investigation on Etelebou Frequent Trips
Aniamaka, Nonso and Miebi Debekeme
Reliability Focal Point, GB-KCR PU

## Slide 2: Timeline of Etelebou Trips Counts in the last 1 Year
Chart: 
| Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | 2020 | 2021
Total | 4 | 1 | 2 | 7 | 6 | 6 | 2 | 2 | 10 | 3 | 5 | 6 | 1 | 1

## Slide 3: Timeline of Etelebou Trips Counts in the last 1 Year
Chart: 
| Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | 2020 | 2021
Total | 4 | 1 | 2 | 7 | 6 | 6 | 2 | 2 | 10 | 3 | 5 | 6 | 1 | 1
CFP upsets
High level in vessels (x3)
Low Pump line Pressure (x3)
Low instrument gas
High pump line Pressure (CPF upsets, post Well test Operations)
RSP failure

## Slide 4: TRIPS RANKED BY CAUSES
Chart: Trips by Causes
| High level in Vessels | Well issues | CPF issues | Trip Cause unspecified | pump issues | Low Instrument gas | Recirculation valve | Low Pumpline (Cause unspecified) | RSP spurious signal | leak - flowline | ESD - QAW valve | Delivery line Pressure - Low | Spurious discharge pressure transmitter | Pumpline Pressure - High | LP Sep 2 MSDV
Count of *Unique Trips Count2 | 12 | 9 | 7 | 6 | 5 | 4 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Count of *Unique Trips Count | 0.21429 | 0.375 | 0.5 | 0.60714 | 0.69643 | 0.76786 | 0.82143 | 0.875 | 0.89286 | 0.91071 | 0.92857 | 0.94643 | 0.96429 | 0.98214 | 1

## Slide 5: TOP TRIPS WITH ASSOCIATED DEFERMENT
Chart: Trip Count
| High level in Vessels | Well issues | CPF issues | Trip Cause unspecified | pump issues | Low Instrument gas | Low Pumpline (Cause unspecified) | Recirculation valve | Spurious discharge pressure transmitter | LP Sep 2 MSDV | ESD - QAW valve | Pumpline Pressure - High | RSP spurious signal | leak - flowline | Delivery line Pressure - Low
Count of *Unique Trips Count | 12 | 9 | 7 | 6 | 5 | 4 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Sum of Deferred Oil plus Cond bbls | 5047.2446 | 177995.9259 | 3181.4076 | 4685.8022 | 5218.6013 | 912.4397 | 3365.0703 | 3652.1668 | 1198.8119 | 645.161 | 268.1267 | 572.939 | 688.7251 | 5723.1173 | 154.7736

## Slide 6: MOST DEFERMENTS COME FROM WELL RELATED ISSUES
Chart: 
Chart: 
| CPF issues | Low Instrument gas | Pumpline Pressure - High | Recirculation valve | Spurious discharge pressure transmitter | Well issues
Total | 3181.4076 | 912.4397 | 572.939 | 3652.1668 | 1198.8119 | 177995.9259

## Slide 7: FINDINGS FROM INVESTIGATION
Entry into SAP (poor)
Low Pump line Pressure
Pumps issues
High Level in Vessels
Well related issues
CPF upsets
Low instrument gas
High Pump line pressures
Quick as a Wink Valve failure

## Slide 8: Low Pump line Pressure
Pump issues
  Pump speed control
    Governor
    Sensing lines issues – Wet gas, liquid in Control lines
    Recirculation valves – passing valve
    Level Control valves of our vessels – Wet gas, liquid in Control lines
    Auto drain valves
Sand in Etelebou process
    From wells
    From Saver pit.

## Slide 9: High Level in Vessel (12) – Risk of LOPC
High Liquid Level Controller
  Pump speed control (as discussed in previous slide)
  Level Controllers of our vessels
    Sensing lines issues – Wet gas, liquid in Control lines
    Auto drain valves of our scrubbers
  Recirculation valves – Wet gas, liquid in Control lines, passing valve

## Slide 10: Reliability Event Abridged Learning (REAL)
What Happened
On 05-05-2021 at 1754hrs, Etelebou FS tripped on Flare Knock Out Vessel High-High Liquid level. Robert Shaw Panel immediately initiated a shutdown of the station.
Causes
From our troubleshooting/5-why/causal investigation, we found the following causes of the failure:
a) The HiHi Level transmitter/controller loop on the Surge Vessel failed to activate an initial trip due to liquid ingress in the control lines. (The eventual trip came from the Flare knock-out vessel liquid HiHi transmitter which is downstream to the surge vessel).
b) The pumps performed well but recirculation valve recycled most of the pump output back into the surge vessel due to level controller loop issues mentioned above.
c) The liquid ingress into flow lines was largely a result of malfunctioned auto-drain valves for Flow station gas scrubbers.
d) Etelebou station feeds from high sand-content wells and this causes passing of recirculation valve.
Corrective Actions
We have identified actions below to address the specific causes highlighted above:
Troubleshoot recirculation-level controller loop. – done
Carry out frequent draining of gas scrubbers to mitigate water ingress into instrument gas control lines.
Troubleshoot or replace recirculation valve (as current valve is passing)
Troubleshoot / replace auto-drain valves in Etelebou.
Check that mitigations are in place to prevent pick-up of sand, dirt and other foreign object during pumping operation from Etelebou saver pit.
Change Etelebou FS control lines from instrument gas usage to instrument air
Mothballing of Etelebou flow station (rerouting all of Etelebou Wells to an LP header takes out the need for bringing in instrument gas)
Scrubber performance needs to be checked.
Consequences
Failure of this equipment caused an oil deferment of 6288bbl for about 3 days, due to community issues that further prevented timely restart of the Flow station.
Image/Illustration
Insert image or illustrative drawing

## Slide 11: ROOT CAUSES
We have identified root causes which if addressed will drive down Etelebou trips by at least 80%:
High sand content in Etelebou (Recirculation and Pump issues)
Auto drain valves (Wet gas and liquids in control line)
Scrubber Efficiency (Wet gas and liquids in control line)
Passing recirculation valve (High levels in vessels)
Pump efficiency (Overhaul as was done on Pump 5)
CPF upsets (High pump line pressure)
Change out of instrument gas to instrument air (Wet gas and liquids in control line)

## Slide 12: RECOMMENDATIONS
We have identified actions below to address the specific causes highlighted above:
Troubleshoot recirculation-level controller loop. – done
Carry out frequent draining of gas scrubbers to mitigate water ingress into instrument gas control lines.
Troubleshoot or replace recirculation valve (as current valve is passing)
Troubleshoot / replace auto-drain valves in Etelebou.
Check that mitigations are in place to prevent pick-up of sand, dirt and other foreign object during pumping operation from Etelebou saver pit.
Change Etelebou FS control lines from instrument gas usage to instrument air
Scrubber performance needs to be checked.
Re-routing Etelebou flow station (rerouting all of Etelebou Wells to an LP header takes out the need for bringing in instrument gas)

## Slide 14: TOP DEFERMENTS RANKED
Chart: Deferment
| Pumpline Pressure - Low | Flowline leak | High level (Vessels) | CPF issues | Pump issue | Level Control (Vessel) | N/A | Pumpline Pressure - High | Spurious discharge pressure transmitter | Recirculation valve | High Pressure - LP Separator | Low instrument gas | QAW valve | RSP failure | Delivery line Pressure Low | Pump speed control
Sum of Deferred Oil plus Cond bbls | 11621.0298 | 5723.1173 | 3384.1285 | 3181.4076 | 2178.7618 | 1663.1162 | 1481.1308 | 1390.7873 | 1198.8119 | 980.4803 | 645.161 | 618.8631 | 601.8394 | 450.7167 | 154.7736 | 40.262
Sum of Deferred Oil plus Cond bbls2 | 0.32907 | 0.49114 | 0.58696 | 0.67705 | 0.73875 | 0.78584 | 0.82778 | 0.86717 | 0.90111 | 0.92888 | 0.94715 | 0.96467 | 0.98171 | 0.99448 | 0.99886 | 1
Low Pumpline Pressure: 11,621.03 bbls
Flowline leak: 5,723.12 bbls
High level in Vessels: 3384.12 bbls