## High Risk for Swamp West Assets
SWAMP WEST ASSET
S/NO | FORCADOS ACTIVITY | Inspection Date | Description | Remedial Actions | Risk | Report Reference | Close out tracking method e.g. SAP, CIMS, FOUNTAIN, ORIP | Notification / Fountain / WO | LAFD/Target Date | Execution Party | Status
1 | FORCADOS JETTY : JETTY SHEET PILES | 2022-01-21 | Severe corrosion with metal loss along section of Jetty facing Jetty security post to front of Underwater Yard | Provide and install new Sheet Piles. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid coat, Polyurethane topcoat or other approved coating materials on the prepared surface. Area = 400 x 2m | H | SCiN-2022-03-00000019
2 | JETTY SHORELINE | 2022-01-21 | Severe subsidence with collapsed concrete pavement along shoreline 29m x 1.5m x 50mm | Excavate collapsed concrete. Provide spread and compact affected section with sharp sand. 29m x 1.5m x 0.9m Provide, cut and fix mild Steel BRC 65 mesh reinforcement in concrete 29m x 1.5m Provide mix and place concrete grade 30 to replace collapsed concrete pavement. 29m x 1.5m x 100mm | H | SCiN-2022-03-00000019
3 | PONTOON GANGWAY/ BOAT LANDING FOR SMALL BOATS | 2022-01-22 | Severely degraded Pontoon Jetty for Light Crafts | Replace. 1No. Pontoon Jetty with Gangway. (Lumpsum) | H | SCiN-2022-03-00000019
| CRUDE LOADING PLATFORM (CLP). | 2022-01-22 | WINDSOCK; Windsock not in place, missing Windsock pole in good condition | Provide and Install missing windsock for the Helideck | H | SCiN-2022-03-00000019
| FORCADOS TERMINAL – CORE ZONE MANIFOLD 5 | 2022-01-22 | Moderately degraded personnel access U – Channel inclined beam. | Replace 1 No. 250mm by 80mm Uchannel beam | H | SCiN-2022-03-00000019 |  | 23007072
OGBOTOBO CONCRETE BARGE
| HP, LP, XHP AND TEST HEADER | 2022-04-03 | Warped section of Grating | Replace warped Grating with new one 2.5m x 0.9m | H | SPDC-2022-04-00000048 |  | 11908763/11908702/11908786
OPUKUSHI FLOWSTATION&WELLHEADS ACTIVITIES
4 | WELL HEAD 21T RISER CLAMP | 2019-03-19 | Failed Riser Support Clamp. 1No. | Provide and install Riser Support Clamp. 1No | H | SPDC-2019-04-00000109 | SAP | 11729244
5 | WELLHEAD PLATFORM N5S UPPER DECK PLATFORM | 2019-03-19 | DAVIT Expired certification. Due date: 10/03/2019 | Recertify Davit. | H | SPDC-2019-04-00000109 | SAP | 11729244
6 | WELL HEAD PLATFORM N2L/S (NOT FLOWING) UPPER DECK PLATFORM | 2019-03-19 | Severe coating failure on Davit. | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat on the prepared surfaces. 100mm dia. CHS, 6.5m long | H | SPDC-2019-04-00000109 | SAP | 11729244
7 |  | 2019-03-19 | HANDRAILS Severe coating failure on Handrails. | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat on the prepared surfaces. 35mm dia. CHS: 2.8m long, 8Nos. Post: 1.2m length, 16Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
8 | WELL HEAD PLATFORM N2L/S (NOT FLOWING) FENDER | 2019-03-19 | Missing and degraded wooden Fenders. | Provide and install rubber Fender, made of Polythene material with Fibre Glass reinforcement. 4Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
9 | WELL HEAD PLATFORM N1L/S UPPER DECK PLATFORM | 2019-03-19 | HANDRAILS Severe coating failure on Handrails Missing Handrails on Deck Platform. Missing Guard Chain | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat on the prepared surfaces. 35mm dia. CHS: (3.7m + 2.8m) x 4Nos. Handrail post: 1.2m length x 16Nos. Provide, weld and install 35mm dia. galvanized CHS as Railings to replace the missing sections. 35mm dia. CHS: 4.4m length Provide and install galvanize Chains: 0.9m length x 3Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
10 |  | 2019-03-19 | DAVIT Severe coating failure on Davit. Expired certification. Due date: 10/03/2019 | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 120mm dia. CHS: 6.5m length. Recertify Davit before use. | H | SPDC-2019-04-00000109 | SAP | 11729244
11 | WELL HEAD PLATFORM N1L/S MAIN ACCESS LADDER. | 2019-03-19 | Severe coating failures on Ladder Members. | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. Ladder flat bars: 6m length, 2Nos. Ladder Rungs: 25mm rod, 0.3m length, 24Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
12 | WELL HEAD PLATFORM N1L/S CASING | 2019-03-19 | Severe corrosion with metal loss on Casing and support Plates. | Remove corrosion with hand tools. Prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.6m dia. CHS: 3m length. Plate dimension: 0.01m thickness, 0.3m width, 1.2m length, 4Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
13 | WELL HEAD PLATFORM N1L/S STRUCTURAL STEEL FRAME MEMBERS | 2019-03-19 | Severe corrosion on Steel Base Plate | Prepare surface with hand tools to remove corrosion from base plate and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.3m width, 1.8m length, 4Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
14 | WELL HEAD PLATFORM N1L/S FENDER | 2019-03-19 | Severely degraded wooden Fenders | Provide and install rubber Fenders, made of Polythene material with Fibre Glass reinforcement. 4Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
15 | WELL HEAD PLATFORM N1L/S LOWER DECK PLATFORM | 2019-03-19 | HANDRAILS Severe coating failure on Handrails. | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 30mm dia. CHS, 3m length, 8Nos. 1m length, 8Nos. Handrail Post: 30mm dia. CHS, Handrail Post: 1.2m length, 24Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
16 |  | 2019-03-19 | Severe coating failures on Deck Platform Structural Steel members. | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 100 x 60mm Channel: 23.2m long | H | SPDC-2019-04-00000109 | SAP | 11729244
17 |  | 2019-03-19 | ACCESS LADDER ON LOWER DECK Severe coating failure on Access Ladder. | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.03m wide, 1.8m long, 4Nos. Ladder Rungs: 0.3m long, 16mm dia. Rod 16Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
18 | WELL HEAD PLATFORM N3L/S DECK PLATFORM | 2019-03-19 | HANDRAILS Severe coating failure on Deck Platform Handrails | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.035m dia. CHS: 3.6m x 8Nos. 1.2m x 16Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
19 | WELL HEAD PLATFORM N12L/S UPPER DECK PLATFORM | 2019-03-19 | HANDRAILS Severe coating failure on Handrails | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.035m dia. CHS: 3.8m x 4Nos. 2.8m x 4Nos, 1.2m x 14Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
20 | WELL HEAD PLATFORM N12L/S FENDERS | 2019-03-20 | Severely degraded wooden Fenders. 4Nos. | Provide and install rubber Fenders, made of Polythene material with Fibre Glass reinforcement 4Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
21 | WELL HEAD PLATFORM N12L/S LOWER DECK PLATFORM | 2019-03-20 | HANDRAILS Severe coating failure on Handrails. | Remove corrosion with hand tools. Prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.035m dia. CHS: 3.7m x 8Nos. 1m x 8Nos. 1.2m x 24Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
22 |  |  | Severe coating failure on lower Deck Ladders | Remove corrosion with hand tools. Prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. Ladder flat bars: 1.8m x 0.03m x 4Nos. Ladder Rungs: 0.3m x 10Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
23 | WELL HEAD PLATFORM 34T UPPER DECK PLATFORM |  | HANDRAILS Severe coating failure on Handrails | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.035m dia. CHS: 3.8m x 4Nos.2.8m x 4Nos, 1.2m x 14Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
24 | WELL HEAD PLATFORM 34T CASING | 2019-03-21 | Severe corrosion with metal loss on Casing | Remove corrosion with hand tools. Prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.6m dia. CHS, 3.5m length. | H | SPDC-2019-04-00000109 | SAP | 11729244
25 |  |  | CASING CLAMP PLATE Severe corrosion on Casing Clamp. | Remove corrosion with hand tools. Prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 1.3m x 0.3m 0.01m (thickness) | H | SPDC-2019-04-00000109 | SAP | 11729244
26 | WELL HEAD PLATFORM 34T LOWER DECK PLATFORM | 2019-03-21 | HANDRAILS Severe coating failure on Handrails | Remove corrosion with hand tools. Prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.035m dia. CHS: 3.7m x 8Nos. 1m x 8Nos. 1.2m x 24Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
27 | CLUSTER WELL HEADS PLATFORM (35T, 36T, 37T, 38T) GAS WELL VALVE MAINTENANCE PLATFORM |  | Broken section of Handrails. | Fabricate and install steel hand rails to replace the broken sections. 0.035m dia. CHS, 2.8m 1No. | H | SPDC-2019-04-00000109 | SAP | 11729244
28 | WELL HEAD PLATFORM 2T FENDER | 2019-03-21 | Missing Fenders. | Provide and install rubber Fenders, made of Polythene material with Fibre Glass reinforcement. 4Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
29 | WELL HEADS PLATFORM 22T FENDERS | 2019-03-21 | Missing Fenders | Provide and install rubber Fender, made up of Polythene material with Fibre Glass reinforcement bar. 4Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
30 | WELL HEADS 33L/S UPPER DECK PLATFORM | 2019-03-21 | HANDRAILS Severe coating failure on Handrails | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat on the prepared surfaces. 0.035m dia. CHS: 3.8m x 4Nos.; 2.8m x 4Nos, 1.2m x 14Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
31 | WELL HEADS 33L/S LOWER DECK PLATFORM | 2019-03-21 | HANDRAILS Missing Handrails on Platform. | Fabricate and install steel hand rails to replace the missing hand rails on the Platform. 0.035m dia. CHS: 4.6m long | H | SPDC-2019-04-00000109 | SAP | 11729244
32 |  |  | Severe coating failure on Handrails. | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.035m dia. CHS: 3.8m x 4Nos.; 2.8m x 4Nos, 1.2m x 14Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
33 |  |  | ACCESS LADDER ON LOWER DECK PLATFORM. Severe coating failures on Ladder. | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. Ladder flat bars: (1.8 x 0.05m) x 4Nos. Ladder Rungs: 0.3m x 10Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
34 | WELL HEADS 32 UPPER DECK PLATFORM |  | HANDRAILS Severe coating failure on Handrails. | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.035m dia. CHS: 3.8m x 4Nos. 2.8m x 4Nos, 1.2m x 14Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
35 | WELL HEADS 32 CASING | 2019-03-21 | Severe corrosion with metal loss on casing. | Remove corrosion with hand tools. Prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.6m dia. CHS, 3m length. | H | SPDC-2019-04-00000109 | SAP | 11729244
36 | WELL HEADS 32 STRUCTURAL STEEL FRAME | 2019-03-21 | Severe corrosion with metal loss on Plate support. | Remove corrosion with hand tools. Prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.3m width x 1.2m x 2Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
37 | WELL HEADS 17L/S UPPER DECK PLATFORM | 2019-03-21 | HANDRAILS Severe coating failure on Handrails. | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.035m dia. CHS: 3.8m x 4Nos. 2.8m x 4Nos, 1.2m x 14Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
38 |  |  | Severe corrosion on Handrail Post support | Remove corrosion with hand tools. Prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.045m dia. CHS: 13Nos x 0.2m | H | SPDC-2019-04-00000109 | SAP | 11729244
39 |  |  | Warped and missing Toe Plates | Provide 10mm thick mild steel, cut to size and install to replace missing Plates. 2.8m x 0.1m x 2Nos. 3.8m x 0.1m x 1No. | H | SPDC-2019-04-00000109 | SAP | 11729244
40 |  |  | DECK PLATFORM STRUCTURAL SUPPORT Severe coating failure on support members. | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 60 x 100mm Channel: 3.8m length x 4Nos. 2.8m x 4Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
41 | WELL HEADS 17L/S FENDER | 2019-03-21 | Severely degraded wooden Fenders. | Provide and install rubber Fender, made up of Polythene material with Fibre Glass reinforcement bar. Fender. 4Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
42 | WELL HEADS 17L/S CASING | 2019-03-21 | Severe corrosion with metal loss on production tube Casing | Remove corrosion with hand tools. Prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.6 dia. CHS, 3m length. | H | SPDC-2019-04-00000109 | SAP | 11729244
43 | WELL HEADS 17L/S STRUCTURAL STEEL FRAME | 2019-03-21 | Severe corrosion with metal loss on bracing Plates supporting the Casing | Remove corrosion with hand tools. Prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.3m x 1.2m x 2Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
44 | WELL HEAD 26 UPPER DECK PLATFORM | 2019-03-21 | HANDRAIL Severe coating failures on Handrails. | Remove degraded coating, prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.035m dia. CHS: 3.8m x 4Nos.; 2.8m x 4Nos, 1.2m x 14Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
45 | WELL HEAD 26 FENDER | 2019-03-21 | Mildly degraded wooden Fenders | Provide and install rubber Fender, made of Polythene Fibre Glass reinforcement bar. 4Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
46 | WELL HEAD 26 LOWER DECK PLATFORM | 2019-03-22 | HANDRAILS Moderate-severe coating failure on Handrails. | Remove degraded coating, prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.035m dia. CHS: 3.7m x 8Nos.; 1m x 8Nos. 1.2m x 24Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
47 | WELL HEAD 6 UPPER DECK PLATFORM | 2019-03-22 | Severe corrosion on Davit Base Plate | Remove corrosion with hand tools. Prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. (300 x 300mm Plate) | H | SPDC-2019-04-00000109 | SAP | 11729244
48 | WELL HEAD 29 UPPER DECK PLATFORM | 2019-03-22 | HANDRAILS Severe coating failure on Handrails. | Remove degraded coating, prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.035m dia. CHS: 3.8m x 4Nos. 2.8m x 4Nos. 1.2m x 14Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
49 | WELL HEAD 29 STRUCTURAL STEEL FRAME | 2019-03-22 | Severe coating failure on structural steel frame. | Remove degraded coating, prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.12m dia. CHS: 1.8m x 10Nos. Base plate: 1.8m x 0.3 x 4Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
50 | WELL HEAD 29 LOWER DECK PERFORM | 2019-03-22 | HANDRAILS. Severe coating failure on Handrails. | Remove degraded coating, prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.035m dia. CHS: 3.7m x 8Nos. 1m x 8Nos. 1.2m x 8Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
51 | WELL HEAD 28T UPPER DECK PLATFORM | 2019-03-22 | HANDRAILS Severe coating failure on Handrails. | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.035m dia. CHS: 3.8m x 4Nos.; 2.8m x 4Nos. 1.2m x 14Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
52 | WELL HEAD 28T FENDER | 2019-03-22 | Missing Fenders | Provide and install rubber Fender, made up of Polythene material with Fibre Glass reinforcement. 4Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
53 | WELL HEAD 28T FENDER | 2019-03-22 | HANDRAIL Severe coating failure on Handrails. | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.035m dia. CHS: 3.7m x 8Nos 1m x 8Nos. 1.2m x 8Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
54 | WELL HEAD 1S UPPER DECK PLATFORM | 2019-03-22 | HANDRAILS Severe coating failure on Handrails. | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.035m dia. CHS: 3.8m x 4Nos. 2.8m x 4Nos. & 1.2m x 14Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
55 | WELL HEAD 27T CASING | 2019-03-22 | Severe corrosion with metal loss on inner section of Casing | Remove corrosion with hand tools. Prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.6m dia. CHS, 3m length. | H | SPDC-2019-04-00000109 | SAP | 11729244
56 | WELL HEAD 13L/S (NOT FLWING) UPPER DECK PLATFORM | 2019-03-22 | HANDRAILS Severe coating failure on Handrails. | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer,Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.035m dia. CHS: 3.8m x 4Nos.; 2.8m x 4Nos. 1.2m x 4Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
57 | WELL HEAD 13L/S (NOT FLWING FENDER | 2019-03-22 | Severely degraded wooden Fenders | Provide and install robust rubber Fenders. 3Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
58 |  |  | Missing Fender | Provide and install rubber Fender, made up of Polythene material with Fibre Glass reinforcement. 1No. | H | SPDC-2019-04-00000109 | SAP | 11729244
59 | WELL HEAD 13L/S (NOT FLWING) LOWER DECK PLATFORM | 2019-03-22 | HANDRAILS Severe coating failure on lower Deck Handrails. | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.035m dia. CHS: 3.7m x 8Nos.; 1m x 8Nos. 1.2m x 24Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
60 | WELL HEAD 11L/S UPPER DECK PLATFORM | 2019-03-22 | HANDRAILS Severe coating failure on Handrails. | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 35mm dia. CHS: 3.8m x 4Nos. 2.8m x 4Nos. & 1.2m x 14Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
61 | WELL HEAD 11L/S LOWER DECK PLATFORM | 2019-03-22 | GRATING Missing Platform Grating | Provide stainless steel Grating, cut to size and install Area = 3 x 1m2 | H | SPDC-2019-04-00000109 | SAP | 11729244
62 |  |  | HANDRAILS Missing Platform Handrails | Fabricate and install steel hand rails to approved design on upper Deck Platform to replace the missing sections. 35mm dia. CHS: 0.9m x 6Nos. & 1m x 8Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
63 |  |  | ACCESS LADDER ON LOWER DECK Missing Platform access Ladder | Provide mild steel plate of specified thickness, cut to size, fabricate Ladder and install to replace the missing Ladder. 100mm flat bar: (1.5 x 0.05m) x 4Nos. Ladder Rungs: 16mm dia. Rod, 0.3m x 10Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
64 | WELL HEAD 10 UPPER DECK PLATFORM | 2019-03-22 | HANDRAILS Severe coating failures on Handrails. | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.035m dia. CHS: 3.8m x 4Nos. 2.8m x 4Nos. 1.2m x 14Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
65 |  |  | ACCESS LADDER ON LOWER DECK Broken secondary Access Ladder. | Provide mild steel plate of specified thickness, cut to size, weld as required and fix /install. Ladder flat bars: 1.8m x 0.05m width x 2Nos. Ladder Rungs: 0.3m x 5Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
66 | WELL HEAD 18L/S (FLOWING WELL) UPPER DECK PLATFORM | 2019-03-22 | HANDRAILS Severe coating failure on Handrails | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.035m dia. CHS, 3.8m x 4Nos. 2.8m x 4Nos. & 1.2m x 14Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
67 |  |  | Severe corrosion with metal loss on Davit Base Plate | Remove corrosion with hand tools. Prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. Area = 0.35m x 0.4m | H | SPDC-2019-04-00000109 | SAP | 11729244
68 | OPUKUSHI WELL HEAD PLATFORM 5 UPPER DECK PLATFORM | 2019-03-22 | HANDRAILS Severe coating failure on Handrails | Remove degraded coating, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 35mm dia. CHS, 3.8m x 4Nos.; 2.8m x 4Nos. & 1.2m x 14Nos. | H | SPDC-2019-04-00000109 | SAP | 11729244
69 |  |  | Severe corrosion with metal loss on Davit Base Plate | Remove corrosion with hand tools. Prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. Area = 0.35m x 0.4m | H | SPDC-2019-04-00000109 | SAP | 11729244
70 | OPUKUSHI WELL HEAD PLATFORM 5 FENDER | 2019-03-22 | Severely degraded Fender | Provide and install rubber Fender, made up of Polythene material with Fibre Glass reinforcement. 1No. | H | SPDC-2019-04-00000109 | SAP | 11729244
71 | SURGE VESSEL 2 | 2020-03-21 | Severe corrosion with metal loss on Surge Vessel Base Plate | Prepare surface with hand tools to remove corrosion and apply self-priming Epoxy primer, Epoxy mid coat, and Polyurethane top coat or other approved coating materials on the prepared surfaces. Area: = 3.22m – (3.142x1.62 )m = 2.2m2 | H | SPDC-2020-04-00000164 | SAP | 11729250
72 | METERING AREA | 2022-04-04 | Severe corrosion with metal loss on drain pan underneath the Metering Skid | Prepare surface with hand tools to remove corrosion and apply self-priming Epoxy primer, Epoxy mid coat, and Polyurethane top coat or other approved coating materials on the prepared surfaces. Area =(1 x 6.4)m + (3 x 0.9)m | H | SPDC-2022-04-00000164 | SAP | 11729250
73 | FLOATING DIESEL STATION. | 2019-03-18 | Severe coating failure on Handrails | Prepare surface with hand tools to remove degraded coat and apply self priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 40mm dia. CHS: 1.4m long, 36Nos. 1m length, 38Nos. | H | SPDC-2019-04-00000109 | SAP | 11729250
75 | CHEMICAL SHED | 2022-04-04 | DRAIN PAN Severe corrosion/metal lose on drain pan. | Prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. Area = 7 x 6.5m | H | SPDC-2022-04-00000164 | SAP | 11729431
| DAVIT | 2022-04-04 | Expired davit certification | Recertify davit before use | H | SPDC-2022-04-00000164
| BAY 4 | 2022-04-04 | Warped Grating support and handrails behind Pump Bay 4 and 5 | Carry out steel repair works to straighten and strengthen warped Grating supports and tilted Handrails 80mm x 80mm EAS; 13.5m long | H | SPDC-2022-04-00000164
| BAY 7 | 2022-04-04 | Unstable grating due to missing grating clips | Provide and replace missing grating clips. 4Nos | H | SPDC-2022-04-00000164
| BANK 2 | 2022-04-04 | SURGE VESSEL 2 Severe corrosion with metal loss on surge vessel base plate | Prepare surface with hand tools to remove corrosion and apply self-priming Epoxy primer, Epoxy mid coat and Polyurethane top coat or other approved coating materials on the prepared surface. Area = 2.2m2 | H | SPDC-2022-04-00000164
| BANK 3 | 2022-04-04 | Unstable grating due to missing grating clips | Provide and install grating clips. 8Nos of grating clips | H | SPDC-2022-04-00000164
| WALKWAY EMBARKMENT BY GAS PLANT | 2022-04-04 | Scouring underneath concrete embankment by the entrance gate | Remove gravel from surface. Brake off concrete embarkment. Provide, spred and compact sharp sand on surface to a depth of 400mm. 3.5m x 1.8m x 0.4m Provide and place BRC reinforce grade 30 concrete and make good 3.5m x 1.8m x 0.1m | H | SPDC-2022-04-00000164
76 | DIESEL TANK SHED BY HOUSE BOAT UNDERGOING REPAIR) | 2019-03-16 | Flaked section of Block wall Bundwalls Severe crack on Dwarf Bundwalls. 1.3m length, 3mm crack width, 5Nos. | Provide mix and place sand/cement mixture on flaked area and make good. 1.2m length x 0.7m width. Provide mix and place sand/cement mixture on crack and make good. 1.3 x 0.003m x 5Nos | H | SPDC-2019-04-00000109 | SAP | 11729431
78 | WALK WAY BEHIND THE FRESH WATER TANK AREA. | 2019-03-17 | Suspended Grating due to failed bolt connection for the Structural support member. Binding wire used to hold the member in place. | Provide missing bolt and reconnect the diagonal support member at its base. 1No. | H | SPDC-2019-04-00000109 | SAP | 11729431
80 | OPUKUSHI JETTY (SAIPEM - BUILT) | 2020-03-21 | Absence of Sheet Piles, shoreline protection. Severely eroded and broken section of concrete shoreline protection | Set up Piling Rig, handle, pitch and drive steel sheet piles in any material except rock to specified depth. Provide and install coated steel Sheet Piles. Prepare surface with hand tools and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces Size = 40m x 12m Provide, mix and place BRCreinforced concrete grade 30 Size = 8.5m x 3m x 0.15m | H | SPDC-2020-12-00000099 | SAP
81 | BANK 2 |  | SURGE VESSEL 2 Severe corrosion with metal loss on Surge Vessel Base Plate | Prepare surface with hand tools to remove corrosion and apply self-priming Epoxy primer, Epoxy mid coat, and Polyurethane top coat or other approved coating materials on the prepared surfaces. Area: = 3.22m – (3.142x1.62)m = 2.2m | H | SPDC-2020-04-00000164
82 | METERING AREA |  | Severe corrosion with metal loss on Drain Pan underneath Metering Skid | Prepare surface with hand tools to remove corrosion and apply self-priming Epoxy primer, Epoxy mid coat, and Polyurethane top coat or other approved coating materials on the prepared surfaces. Area =(1 x 6.4)m + (3 x 0.9)m | H | SPDC-2020-04-00000164
| TUNU CPF ACTIVITIES |  | Severe corrosion with metal loss on cable/tubing tray supports – equal angle steel supports under the Wellhead cluster platform | Remove corrosion with hand tools, prepare surface and apply self-priming Epoxy primer, polyurethane topcoat or other approved coating materials on the prepared surfaces. 50 x 50mm EAS, 7.5m x 0.2m |  | SPDC-2021-09-00000005 |  | 11909068
| FLARE STRUCTURE FLARE IGNITION POINT | 2022-04-02 | Scouring around concrete foundation. Depth of scouring: 200mm | Provide and fill up scoured area with sharp 15m x 1.4m x 0.8m | H | SPDC-2022-04-00000047 |  | 11909068
|  | 2022-04-02 | Electrical panel box shed behind flare ignition point Warped steel stanchion and differential settlement of concrete foundation due to subsidence | Monitor level of subsidence. Replace warped steel section with one (50 x 100)mm PFC, 2.8m x 2Nos. Reconstruct concrete foundation using reinforced C30 concrete. 400 x 400 x 500mm x 2Nos. | H | SPDC-2022-04-00000047 |  | 11909068
| FLARE STRUCTURE | 2022-04-02 | Scouring on foundation of pipe rack close to flare | Provide and fill up scoured area with sharp 2.5m x 2m x 0.3m | H | SPDC-2022-04-00000047 |  | 11909068
| PIGGING AREA | 2022-04-02 | Failed concrete floor due to subsidence. Suspended personal access staircase due to subsidence on concrete floor. (Suspended depth 180mm) | Demolish and cart away concrete floor. Provide and install concrete kerbs on perimeter of pigging platform area. 34m x 1m x 0.15m Provide and install concrete supports at personal access staircase. 0.5m x 1.5m x 8Nos. Gravel dress underneath pigging platform and make good 24m x 10m x 0.6m | H | SPDC-2022-04-00000047 |  | 11909068
| PIG RECEIVER 1 (TUNG 1-A-2304 NAG FOR DODO NORTH) | 2022-04-02 | Suspended stanchion pipe support due to subsidence of concrete plinth S.R 50mm. | Monitor level of subsidence periodically. Provide and place neoprene packs at the space between stanchion and concrete plinth. | H | SPDC-2022-04-00000047 |  | 11909068
| PIG RECEIVER 2 (FOR OPUKUSHI, BENISEDE AND OGBOTOBO) | 2022-04-02 | Suspended pipe supports. Subsidence on concrete foundation Subsidence range = 50mm | Provide and place neoprene packs in space between stanchion and concrete plinth. Monitor level of subsidence periodically | H | SPDC-2022-04-00000047 |  | 11909068
|  | 2022-04-02 | Failed/tilted concrete foundation and pipe supports due to subsidence | Reconstruct concrete foundations using C30 reinforced concrete aligning to support flow line | H | SPDC-2022-04-00000047 |  | 11909068
| CHEMICAL SHED | 2022-04-02 | Steel Gate: Severe cracks with exposed rebars on concrete plinths | Recast concrete plinths using grade 30 concrete 380mm x 350mm x 270mm x 2Nos. | H | SPDC-2022-04-00000047 |  | 11909068
|  | 2022-04-02 | Base of walls detaching from foundation as a result of subsidence on concrete foundation. Subsidence range = 50mm. | Provide, mix and treat detached wall base with cement and sand or mortar mix. 5.5m x 0.225m x 25mm Monitor level of subsidence periodically | H | SPDC-2022-04-00000047 |  | 11909068
| ELEVATED WATER TANK | 2022-04-02 | Severe corrosion with metal loss on primary support beams for overhead tank | Provide stiffeners and reinforce defective section of steel flange 203mm x 133mm I-Beam, 2.5m x 3Nos. | H | SPDC-2022-04-00000047 |  | 11909068
|  | 2022-04-02 | Spalling on concrete plinths. | Remove and cart away spalled concrete. Provide, mix and treat Spalled section with cement sand mortar Size = 1m x 0.28m x 2mm x 8Nos | H | SPDC-2022-04-00000047 |  | 11909068
|  | 2022-04-02 | Suspended concrete foundation due to severely eroded soil | Provide and lay sharp sand around tank foundation to a depth of 300mm. 6.5m x 4.5m x 0.3m Provide, mix and place reinforced concrete grade 30 to a depth of 150mm 6.5m x 4.5m x 0.15m | H | SPDC-2022-04-00000047 |  | 11909068
| HELIPAD WALKWAY SHED | 2022-04-02 | Severely corroded guard rail by drainage close to shed | Prepare surface and apply selfpriming Epoxy primer, Epoxy mid-coat and Polyurethane topcoat or other approved coating materials to the prepared surfaces 80mm dia. CHS; 1.8m x 22Nos. | H | SPDC-2022-04-00000047 |  | 11909068
| TUNU JETTY | 2022-04-02 | Jetty Ramp Broken gate hinges and pivot screw | Provide and install by welding new steel hinges to gate 2Nos. Provide and install pivot screw | H | SPDC-2022-04-00000047 |  | 11909068
|  | 2022-04-02 | Loosed wire gaze on gate of jetty ramp | Weld properly wire gaze to steel gate | H | SPDC-2022-04-00000047 |  | 11909068
|  | 2022-04-02 | Silted jetty shore line from ramp jetty to CPF fence | Carry out dredging activity alone the shore line 160m x 8m width x 3m depth | H | SPDC-2022-04-00000047 |  | 11909068
|  | 2022-04-02 | Broken section of jetty wall | Remove and cart away broken/loosed concrete from jetty wall and repair broken wall section 1.2m x 1.5m x 0.2m | H | SPDC-2022-04-00000047 |  | 11909068
| PERIMETER FENCE | 2022-04-02 | Missing and degraded chain-link fence by military camp close to FLB | Remove and cart away degraded chain-link fence and post. Provide and install citadel fence 80m x 3m | H | SPDC-2022-04-00000047 |  | 11909068
|  | 2022-04-02 | Shoreline chain-link fence Severe corrosion on steel post. Degraded and broken chain link fence | Remove and cart away degraded chain-link fence and steel post. Provide and install citadel fence supported by reinforced grade 30 concrete foundations and beams 300m x 3m | H | SPDC-2022-04-00000047 |  | 11909068
| CABLE TRAY SUPPORT | 2021-08-06 | Severe corrosion with metal loss on cable/tubing tray supports – equal angle steel supports under the Wellhead cluster platform | Remove corrosion with hand tools, prepare surface and apply self-priming Epoxy primer, polyurethane topcoat or other approved coating materials on the prepared surfaces. 50 x 50mm EAS, 7.5m x 0.2m | H | SPDC-2021-09-00000005
| TUNU 1 WELLHEAD PLATFORM (COMPLETELY VANDALIZED) BOAT LANDING | 2021-08-06 | Fenders Missing Fenders | Provide and install Rubberized Wharf Fenders, made up of Polythene materials with fiber glass reinforcement bars. 0.2 x 0.2 x 2.5m x 4Nos. | H | SPDC-2021-09-00000005
| TUNU 1 WELLHEAD PLATFORM (COMPLETELY VANDALIZED). LOWER DECK PLATFORM | 2021-08-06 | Warped and completely bent out of shape Grating supports, Handrails and Toe boards | Remove and cart away warped members of lower deck Platform. Provide and install/weld steel sections as required. Prepare surface and apply selfpriming epoxy primer, polyurethane topcoat or other approved coating materials on the prepared surfaces. Grating support: 100mm dia CHS, 10.4m length. 100 x 60mm channel, 21.8m length. Toe board: 4.1m x 0.1m x 4Nos.Handrails: 35mm dia CHS, 57.8m length. | H | SPDC-2021-09-00000005
|  | 2021-08-06 | Access ladder Missing Access Ladder due to vandalization of platform | Provide and install Ladder on lower deck. Prepare surface and apply selfpriming epoxy primer, polyurethane topcoat or other approved coating materials on the prepared surfaces 70 x 70mm EAS, 1.7m x 4Nos. Ladder rungs: 35mm dia bar, 0.3m x 10Nos. | H | SPDC-2021-09-00000005
| TUNU 3 WELLHEAD PLATFORM LOWER DECK PLATFORM | 2021-08-06 | Severely warped Grating Platforms, Grating supports, Handrails and Toe boards | Remove and cart away warped members of lower deck Platform. Provide and install/weld steel sections as required. Prepare surface and apply selfpriming epoxy primer, polyurethane topcoat or other approved coating materials on the prepared surfaces. Grating: 3m x 1.2m x 2Nos. Grating support: 100mm dia. CHS, 10.4m length. 100 x 60mm channel, 21.8m length. Toe board: 4.1m x 0.1m x 4Nos. Handrails: 35mm dia. CHS, 57.8m length. | H | SPDC-2021-09-00000005
83 | EXTERNAL PART OF A-BLOCK BUILDING SUSPENDED CEILING PANEL ON THE PERIMETER EAVE | 2019-03-23 | Failed/collapsed section of the Aluminium Ceiling panel. | Replace and screw to firmly fix the Aluminium Ceiling panel to the Ceiling rails. | H | SPDC-2019-04-00000193 | SAP | 11729263
84 | EXTERNAL PART OF OFFICE BLOCK BUILDING | 2019-03-24 | Severe subsidence of fill on perimeter Apron 68m length, 1.3m width, 0.5m depth. X 2Nos. | Excavate to 0.5m depth - the earth fill and the eroded sections. Provide, fill the excavated section with gravel/chippings to replace the earthfill and serve as new finishing for the Apron. Vol. = (68 x 1.3 x 0.5m) x 2No. | H | SPDC-2019-04-00000193 | SAP | 11729263
85 | SEWAGE TREATMENT PLANT (STP PLANT) | 2019-03-26 | Dosing Chamber Tilted Chamber due to severe subsidence around the dosing Chamber | Remove and store/place in a safe place dozing Chamber and baggage unit. Excavate and cart away existing concrete floor to a depth of 0.25m. Fill spread and compact sharp sand to a depth of 0.1m. Provide, mix, place and compact green reinforced concrete as raft foundation as specified. Vol. = 5.8 x 1.4 x 0.15m | H | SPDC-2019-04-00000193 | SAP | 11729263
86 | CIVILSTRUCT ASSET INTEGRITY ASSESSMENT OF ELEVATED WATER TANK FOUNDATION | 2019-03-01 | Severe scouring at the base of the concrete foundation for the Water Tank Steel Support Structures. Cracks on concrete pavement around the column bases due to the eroded support materials. Pavement - 9.9m x 0.7m x 0.15m | Demolish and cart away top side of degraded concrete. Fill eroded sections with sand and compact appropriately. L =9.9m, W =0.7m, D = 0.5m (1.73m3) Prepare & cast grade C20 Concrete Plinth, complete with reinforcement to replace damaged Plinth (2.66m3) | H | SPDC-2019-04-00000142 | SAP | 11729263
87 | CABLE TRAY SUPPORTS TUNU WELLHEAD CLUSTER PLATFORM | 2019-07-17 | Severe corrosion with metal loss on cable/tubing tray supports - equal angle steel supports under the Wellhead Cluster Platform | Remove corrosion with hand tools, prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 50 x 50mm EAS, 7.5m x 0.2m | H | SPDC-2019-07-00000214 | SAP | 11729263
88 | FENDERS TUNU 1 WELLHEAD PLATFORM (INACTIVE WELL) | 2019-07-18 | Severely degraded and missing wooden Fenders. | Provide and install Rubber Wharf Fenders, made of Polythene materials with fiber glass reinforcement bars. 0.2 x 0.2 x 2.5m x 4Nos. | H | SPDC-2019-07-00000214 | SAP | 11729263
ESTUARY FLOWSTATION ACTIVIES
89 | ESTUARY - HELIDECK PLATFORM | 2020-07-18 | PERIMETER SAFETY NET Torn perimeter Safety Net at various sections. | Replace torn chain-link Safety Net along sections affected. Area = 34.4 x 1.25 x 2Nos | H | SPDC-2020-08-00000079 | SAP | 11742456
90 |  | 2020-07-18 | TIE DOWN POINT Severe corrosion/metal loss on tie down points. | Provide, cut to length steel bars for helicopter anchor points. prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 25mm dia. CHS, 0.3m x 12Nos. | H | SPDC-2020-08-00000079 | SAP | 11742456
91 |  | 2020-07-18 | FIRE EXTINGUISHER Holder Severe corrosion and coating failure on fire extinguisher holder. | Remove corrosion with hand tools, prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 60 x 60mm EAS: 1.45m x 2Nos. 0.7m x 2Nos. 1.5m x 2nos. 1.45m x 0.7 x 3Nos. 60mm dia. CHS, 2.2m x 3Nos. | H | SPDC-2020-08-00000079 | SAP | 11742456
92 | WELL HEAD CLUSTER 5A CABLE TRAY SUPPORT | 2019-05-20 | Severely corroded sections of Cable Tray support with metal loss. | Remove corrosion with hand tools, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 80 x 50mm Channel, 0.4m x 10Nos 60 x 60mm EAS, 1m x 10Nos. | H | SPDC-2019-07-00000086 | SAP | 11742481
93 | WELL HEAD CLUSTER 5 FENDER | 2019-05-20 | Severely damaged rubber Fender. | Provide and install Rubber Wharf Fenders, made of Polythene materials with fiber glass reinforcement bars. 0.3 x 0.3 x 0.3m x 4m x 1No. | H | SPDC-2019-07-00000086 | SAP | 11742481
94 | CLUSTER 42 UPPER DECK | 2019-05-20 | Missing steel members: | Provide universal Beam and gusset Plates of specified dimensions, cut to size and install. 500 x 300mm I-Beam, 2.5m x 2 Nos. 300x15 0mm I-Beam, 2.5m x 6 Nos. Gusset Plates (500 x 500mm) 10Nos. Chequered Plate (3x1.5m) | H | SPDC-2019-07-00000086 | SAP | 11742481
95 | CLUSTER 42 PLATFORM LADDER | 2019-05-20 | Severe corrosion on Aaccess Ladder. | Remove corrosion with hand tools, prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 50mm dia. CHS, 3.5m x 2Nos. Ladder rungs: 16mm dia. CHS, 0.3m x 12Nos. | H | SPDC-2019-07-00000086 | SAP | 11742481
96 | CLUSTER 42 CASING | 2019-05-20 | Severely corroded Casing. | Remove corrosion with hand tools, prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 1200mm dia. CHS, 6m x 4Nos. | H | SPDC-2019-07-00000086 | SAP | 11742481
97 | CLUSTER 42 BOAT LANDING | 2019-05-20 | Severe corrosion on steel Gratings, Handrails and structural support members, toe Plate. | Remove corrosion with hand tools, prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. Gratings. 4.5m x 1.1m. Handrails. 40mm dia. CHS, 1m x 12Nos., 2m x 6Nos., 0.8m x 8Nos. Structural Support Members 180 x 180mm Channel, 1.2m x 2Nos. 250mm dia. CHS, 44m length. 300mm dia. CHS, 46m length. Toe Plate 200 x 200mm E.A, 35m Length. | H | SPDC-2019-07-00000086 | SAP | 11742481
98 | CLUSTER 42 FENDER | 2019-05-20 | Severely degraded Fenders. | Provide and install Rubber Wharf Fenders, made of Polythene materials with fiber glass reinforcement bars. (6Nos.) | H | SPDC-2019-07-00000086 | SAP | 11742481
99 | WELLHEAD CLUSTER 2 FENDER | 2019-05-20 | Severely degraded rubber Fenders. | Remove severely degraded Fenders. Provide and install rubber wharf Fender. (2Nos.) | H | SPDC-2019-07-00000086 | SAP | 11742481
100 | WELLHEAD CLUSTER 93 LOWER DECK CENTER PLATFORM | 2019-05-20 | Moderate to severe corrosion on deck structural support members. | Remove corrosion with hand tools, prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 400mm CHS, 1.5m long x 4 Nos. 200mm CHS, 2m long x 6 Nos. Gratings (2mx2m) 100x100mm EA, 1.2m long x 6Nos. 180mm dia. CHS, 3m length x 2 Nos. 180mm dia. CHS, 3.2m long x 6 Nos. | H | SPDC-2019-07-00000086 | SAP | 11742481
101 | WELLHEAD CLUSTER 93 PLATFORM LADDER | 2019-05-20 | Severe corrosion on access Ladder. | Remove corrosion with hand tools, prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 50mm dia. CHS, 3.5m x 2Nos. Ladder rungs: 16mm dia. CHS, 0.3m x 12Nos. | H | SPDC-2019-07-00000086 | SAP | 11742481
102 | WELLHEAD CLUSTER 93 BOAT LANDING | 2019-05-20 | Severe corrosion on steel Gratings, Handrails and structural support members, toe Plate. | Remove corrosion with hand tools, prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. Gratings.4.5m x 1.1m. Handrails. 40mm dia. CHS, 1m x 12Nos., 2m x 6Nos. 0.8m x 8Nos. Structural steel support 180 x 180mm channel, 1.2m x 2Nos. 250mm dia. CHS, 44m length. 300mm dia. CHS, 46m length. Toe Plate 200 x 200mm E.A, 35m Length. | H | SPDC-2019-07-00000086 | SAP | 11742481
103 | WELLHEAD CLUSTER 93 FENDER | 2019-05-20 | Severely degraded Fenders. | Provide and install Rubber Wharf Fenders, made up of Polythene materials with fiber glass reinforcement bars. (2Nos.) | H | SPDC-2019-07-00000086 | SAP | 11742481
104 | WELLHEAD CLUSTER 1 UPPER DECK | 2019-05-20 | Severe corrosion on deck platform support members: | Remove corrosion with hand tools, prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 500 X 300mm I-Beam, 1.5m x 4 Nos. 2.5m x 2 Nos. 300 x 150mm I-Beam, 2.5m x 6 Nos. Gusset Plates(500x500mm) 10Nos. Chequered Plate (3x1.5m) Handrails 30mm CHS 42m | H | SPDC-2019-07-00000086 | SAP | 11742481
105 | WELLHEAD CLUSTER 1 LOWER DECK CENTER PLATFORM | 2019-05-20 | Moderate to severe corrosion on structural members. | Remove corrosion with hand tools, prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 400mm CHS, 1.5m Length x 4 Nos. 200mm CHS, 2m length x 6 Nos. Gratings; 2 x 2m 100 x 100mm EA, 1.2m Long x 6Nos. 180mm dia. CHS, 3m long x 2 Nos. 180mm dia. CHS, 3.2m Length x 6 Nos. | H | SPDC-2019-07-00000086 | SAP | 11742481
106 | WELLHEAD CLUSTER 1 PLATFORM LADDER | 2019-05-20 | Severe corrosion on access Ladder. | Remove corrosion with hand tools, prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 50mm dia. CHS, 3.5m x 2Nos. Ladder rungs: 16mm dia. CHS, 0.3m x 12Nos. | H | SPDC-2019-07-00000086 | SAP | 11742481
107 | WELLHEAD CLUSTER 1 CASING | 2019-05-20 | Severe coating failure. | Prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 1200mm dia. CHS, 6m x 4Nos. | H | SPDC-2019-07-00000086 | SAP | 11742481
108 | WELLHEAD CLUSTER 1 BOAT LANDING | 2019-05-20 | Severe corrosion on steel Gratings, Handrails and structural support members, toe Plate. | Remove corrosion with hand tools, prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. Gratings. 4.5m x 1.1m. Handrails.40mm dia. CHS, 1m x 12Nos. 2m x 6Nos. 0.8m x 8Nos. Structural steel support 180 x 180mm channel, 1.2m x 2Nos. 250mm dia. CHS, 44m length. 300mm dia. CHS, 46m length. Toe Plate 200 x 200mm E.A, 35m Length. | H | SPDC-2019-07-00000086 | SAP | 11742481
109 | WELLHEAD CLUSTER 1 FENDER | 2019-05-20 | Severely degraded Fenders. | Provide and install Rubber Wharf Fenders, made up of Polythene materials with fiber glass reinforcement bars. (2Nos.) | H | SPDC-2019-07-00000086 | SAP | 11742481
110 | WELLHEAD CLUSTER 4 LOWER DECK CENTER PLATFORM | 2019-05-20 | Moderate to severe corrosion on Support structures. | Remove corrosion with hand tools, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 400mm CHS, 1.5m Length x 4 Nos. 200mm CHS, 2m length x 6 Nos. Gratings (2mx2m) 100 x 100mm EA, 1.2m Length x 6Nos. 180mm dia. CHS, 3m long x 2 Nos. 180mm dia. CHS 3.2m Length x 6 Nos. | H | SPDC-2019-07-00000086 | SAP | 11742481
111 | WELLHEAD CLUSTER 4 PLATFORM LADDER | 2019-05-20 | Severe corrosion on access Ladder. | Remove corrosion with hand tools, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 50mm dia. CHS, 3.5m x 2Nos. Ladder rungs: 16mm dia. CHS, 0.3m x 12Nos. | H | SPDC-2019-07-00000086 | SAP | 11742481
112 | WELLHEAD CLUSTER 4 CASING | 2019-05-20 | Severe corrosion with metal loss on Casing. | Remove corrosion with hand tools, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 1200mm dia. CHS, 6m x 4Nos. | H | SPDC-2019-07-00000086 | SAP | 11742481
113 | WELLHEAD CLUSTER 4 BOAT LANDING | 2019-05-20 | Failed/Collapsed Boat Landing Platform. | Fabricate and install boat-landing structure in place of the failed structures. Gratings. 4.5m x 1.1m. Handrails. 40mm dia. CHS, 1m x 12Nos., 2m x 6Nos. 0.8m x 8Nos. Structural steel support 350mm dia. CHS, 3.5m x 4Nos. 200mm dia. CHS, 3m x 6Nos. 120mm dia. CHS, 3m x 6Nos. 120mm dia. CHS, 3.2m x 6Nos. Toe Plate 200 x 200mm E.A, 35m Length. | H | SPDC-2019-07-00000086 | SAP | 11742481
114 | WELLHEAD CLUSTER 4 FENDER | 2019-05-20 | Missing Fender and Fender support. | Provide and install Rubber Wharf Fenders, made up of Polythene materials with fiber glass reinforcement bars. (7Nos.) Fabricate and install Fender supports to the cluster frame structure. Fender supports: 300mm CHS vertical 4 Nos 2.5m Long 3 Nos 1.5m Long. | H | SPDC-2019-07-00000086 | SAP | 11742481
115 | WELLHEADS CLUSTER 69 LOWER DECK CENTER PLATFORM | 2019-05-20 | Severe corrosion on structural support members. | Remove corrosion with hand tools, prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces.400mm CHS, 1.5m long x 4 Nos. 200mm CHS, 2m long x 6 Nos. 100x100mm EA, 1.2m long 6Nos. 180mm CHS, 3m long x 2Nos. 180mm CHS 3.2m long x 6Nos. | H | SPDC-2019-07-00000086 | SAP | 11742481
116 | WELLHEADS CLUSTER 69 CASING | 2019-05-20 | Severe coating failure on Casing. | Prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 1200mm dia. CHS, 6m x 4Nos. | H | SPDC-2019-07-00000086 | SAP | 11742481
117 | WELLHEADS CLUSTER 69 BOAT LANDING | 2019-05-20 | Moderate to severe corrosion on steel Gratings, Grating supports, Handrails and structural support members. | Remove corrosion with hand tools, prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. Grating supports 250mm dia. CHS, 4.5m x 2Nos. Grating 1m x 8m Toe Plate -200x200mm E.A, 35m long Gratings. 4.5m x 1.1m. Handrails. 40mm dia. CHS, 1m x 12Nos., 2m x 6Nos. 0.8m x 8Nos. Structural steel support 350mm dia. CHS, 3.5m x 4Nos. 200mm dia. CHS, 3.5m x 6Nos. 300mm dia. CHS, 3.5m x 6Nos. 300mm dia. CHS, 3.5m x 6Nos. | H | SPDC-2019-07-00000086 | SAP | 11742481
118 | WELLHEADS CLUSTER 69 FENDER | 2019-05-20 | Severe coating failure and corrosion on steel supports.Severely degraded Fender. | Remove corrosion with hand tools, prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. Fender supports: 300mm CHS vertical 4 Nos 2.5m Long, 3 Nos 1.5m Long.Provide and install Rubber Wharf Fenders, made up of Polythene materials with fiber glass reinforcement bars (7Nos.) | H | SPDC-2019-07-00000086 | SAP | 11742481
119 | WELLHEAD CLUSTER 51 UPPER DECK | 2019-05-20 | Severe corrosion on deck platform support structures. | Remove corrosion with hand tools, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 500 X 300mm I-Beam, 1.5m x 4 Nos. 2.5m x 2 Nos. 300 x 150mm I-Beam, 2.5m x 6 Nos. Gusset Plates; 500 x 500mm x 10Nos. Chequered Plate; 3 x 1.5m Handrails; 30mm CHS, 45m long. | H | SPDC-2019-07-00000086 | SAP | 11742481
120 | WELLHEAD CLUSTER 51 LOWER DECK CENTER PLATFORM | 2019-05-20 | Moderate to severe corrosion on structural members. | Remove corrosion with hand tools, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 400mm CHS, 1.5m long x 4 Nos. 200mm CHS, 2m long x 6 Nos. Gratings; 2m x 2m 100x100mm EA; 1.2m long x 6Nos. 180mm dia. CHS; 3m long x 2 Nos. 180mm dia. CHS; 3.2m long x 6 | H | SPDC-2019-07-00000086 | SAP | 11742481
121 | WELLHEAD CLUTER 51 PLATFORM LADDER | 2019-05-20 | Severe corrosion on access Ladder. | Remove corrosion with hand tools, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 50mm dia. CHS, 3.5m x 2Nos. Ladder rungs: 16mm dia. CHS, 0.3m x 12Nos. | H | SPDC-2019-07-00000086 | SAP | 11742481
122 | WELLHEAD CLUTER 51 CASING | 2019-05-20 | Moderately corroded Casing. | Remove corrosion with hand tools, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 1200mm dia. CHS, 6m x 4Nos. | H | SPDC-2019-07-00000086 | SAP | 11742481
123 | WELLHEAD CLUTER 51 BOAT LANDING | 2019-05-20 | Severe corrosion and coating failure on steel Gratings, Handrails and structural support members, toe Plate. | Remove corrosion by grit blasting, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. Gratings; 4.5m x 1.1m. Handrails; 40mm dia. CHS, 30.5m long Handrails post. 40mm dia. CHS, 27.5 1m x 12Nos. 2m x 6Nos. 0.8m x 8Nos. Structural steel support 180 x 180mm channel, 1.2m x 2Nos. 250mm dia. CHS, 44m long 300mm dia. CHS, 46m long Toe Plate 200 x 200mm E.A, 35m Length. | M | SPDC-2019-07-00000086 | SAP | 11742481
124 | WELLHEAD CLUTER 51 FENDER | 2019-05-20 | Severely degraded Fenders. | Provide and install Rubber Wharf Fenders, made up of Polythene materials with fiber glass reinforcement bars. (2Nos.) | M | SPDC-2019-07-00000086 | SAP | 11742481
125 | WELLHEAD CLUSTER 103 UPPER DECK | 2019-05-20 | Severe coating failure on deck platform, deck platform structural supports members: | Prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 500 X 300mm I-Beam, 1.5m x 4 Nos. 2.5m x 2 Nos. 300 x 150mm I-Beam, 2.5m x 6 Nos. Gusset Plates; 500 x 500mm x 10Nos. | M | SPDC-2019-07-00000086 | SAP | 11742481
126 | WELLHEAD CLUSTER 103 LOWER DECK CENTER PLATFORM | 2019-05-20 | Moderate to severe corrosion on structural members. | Remove corrosion by grit blasting, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 400mm CHS, 1.5m long x 4 Nos. 200mm CHS, 2m long x 6 Nos. Gratings; 2m x 2m 100x100mm EA, 1.2m long x 6Nos. 180mm dia. CHS; 3m long x 2 Nos. 180mm dia. CHS; 3.2m long x 6 Nos. | M | SPDC-2019-07-00000086 | SAP | 11742481
127 | WELLHEAD CLUSTER 103 PLATFORM LADDER | 2019-05-20 | Severe corrosion on access Ladder. | Remove corrosion with hand tools, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 50mm dia. CHS, 3.5m x 2Nos. Ladder rungs: 16mm dia. CHS, 0.3m x 12Nos. | M | SPDC-2019-07-00000086 | SAP | 11742481
128 | WELLHEAD CLUSTER 103 CASING | 2019-05-20 | Severely corroded Casing. | Remove corrosion with hand tools, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 1200mm dia. CHS, 6m x 4Nos. | M | SPDC-2019-07-00000086 | SAP | 11742481
129 | WELLHEAD CLUSTER 103 BOAT LANDING | 2019-05-20 | Severe corrosion and coating failure on steel Gratings, Handrails and structural support members, toe Plate. | Remove corrosion by grit blasting, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. Gratings; 4.5m x 1.1m. Handrails; 40mm dia. CHS, 30.5m long Handrails post. 40mm dia. CHS, 27.5 1m x 12Nos. 2m x 6Nos. 0.8m x 8Nos. Structural steel support 180 x 180mm channel, 1.2m x 2Nos. 250mm dia. CHS, 44m length. 300mm dia. CHS, 46m length. Toe Plate; 200 x 200mm E.A, 35m long | M | SPDC-2019-07-00000086 | SAP | 11742481
130 | WELLHEAD CLUSTER 103 FENDER | 2019-05-20 | Severe corrosion and coating failure on Fender support. | Remove corrosion by grit blasting, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. Fender supports: 300mm CHS vertical 4 Nos 2.5m long 3 Nos 1.5m long. | M | SPDC-2019-07-00000086 | SAP | 11742481
131 | ESTUARY FLOWSTATION FODP BOAT LANDING | 2020-07-18 | Severely corroded Grating platform. | Remove and cart away corroded Grating from site. Provide galvanized steel Grating, cut to size and install and make good. Area = 12.6m x 1.3m | H | SPDC-2020-08-00000079 | SAP | 11742481
132 |  | 2020-07-18 | Severely degraded rubber Fenders. | Remove corrosion by grit blasting, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 80 x 80mm EAS: 7.2m x 2Nos. 1.3m x 6Nos. 90 x 90mm EAS, 4m x 2Nos. 280mm dia. CHS, 2.2m x 2Nos. 1.4m x 2Nos. 4m x 2Nos. 7m x 2Nos | H | SPDC-2020-08-00000079 | SAP | 11742481
133 |  | 2020-07-18 | FENDER/FENDER SUPPORTS Severe corrosion/coating failure on Fender supports | Remove corrosion by grit blasting, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 100 x 150mm Channel, 8m x 1.3m x14Nos. | H | SPDC-2020-08-00000079 | SAP
134 |  | 2020-07-18 | Severely degraded rubber Fenders | Remove severely degraded Fenders. Provide and install Rubberized Wharf Fenders, made up of Polythene materials with fiber glass reinforcement bars. 0.3 x 0.3 x 2.5m x 7Nos | H | SPDC-2020-08-00000079 | SAP
135 | ESTUARY FLOWSTATION GRATING PLATFORM OPPOSITE WALK WAY TO OLD PROCESS AREA | 2020-07-18 | Severely deflected Grating Platform due largely spaced Grating supports | Provide Grating supports along the short span direction. 80mm x 80mm EAS, 2.2m x 2Nos. & 1.2m x 2Nos. Provide and install galvanized Grating. Area = 3.3m x 2.2m | H | SPDC-2020-08-00000079 | SAP | 11742682
136 | ESTUARY FLOWSTATION PROCESS AREA | 2020-07-18 | Severe corrosion with metal loss on sheds covering Electrical Control Panel | Fabricate and install a new Roof/Aluminium Shed for the panel in place of the degraded one. Prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces Area = 1.3 x 1m | H | SPDC-2020-08-00000079 | SAP | 11742682
137 |  | 2020-07-18 | Warped/bent over-head IPE 200 Beam. | Provide universal Beam of specified dimensions, cut to size and fix including welding/ bolting. IPE 200 Beam, 6m length. | H | SPDC-2020-08-00000079 | SAP | 11742682
138 |  | 2020-07-18 | Shaky Handrail near hook up Manifold Skid. | Remove failed welded point at the base of the rail. Provide railings and bolting connections. Tighten and make good 50mm dia., CHS – 15m. | H | SPDC-2020-08-00000079 | SAP | 11742682
139 |  | 2020-07-18 | DRAIN PAN Severe corrosion with perforation on drain pan underneath process area. | Provide mild steel plate cut to size, weld onto existing pan to strengthen and cover degraded area. Area = 20m x 12m | H | SPDC-2020-08-00000079 | SAP
140 |  | 2020-07-18 | Severe pitting corrosion and coating failure on underside of deck. | Remove corrosion by grit blasting, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 42m x 22m | H | SPDC-2020-08-00000079 | SAP | 11742682
141 | ESTUARY FLOWSTATION OLD FLARE STACK PLATFORM | 2020-07-18 | Severely warped/bent Grating steps (thread). | Provide galvanized steel Grating, cut to size and install. 0.8 x 0.2m x 12Nos. | H | SPDC-2020-08-00000079 | SAP | 11742682
142 |  | 2020-07-18 | Excessively deflected Grating platform due to widely spaced supports. | Provide galvanized steel Grating, cut to size and install. 3.3m x 2.2m. Provide Equal Angles of specified dimensions, cut to size and install to serve as supports at mid span for the Gratings. Prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 80 x 80mm EAS, 2.2m x 2Nos. & 1.2m x 2Nos. | H | SPDC-2020-08-00000079 | SAP | 11742682
143 | ESTUARY FLOWSTATION PILE FOUNDATION (Underneath Process Area). | 2020-07-18 | Severely corrosion with metal loss on Beams and Diagonal Supports for Platform Gratings underneath Process Area | Replace severely corroded and degraded horizontal/diagonal bracings. 300mm dia. CHS; 28m length 250 x 150mm RHS, 7m length 250 x 250mm IPE Beam, 9.5m length | H | SPDC-2020-08-00000079 | SAP | 11742682
144 |  | 2020-07-18 | Severely warped Gratings on access staircase to the process area. | Replace severely warped Gratings on personnel access staircase. 1 x 0.2m x 10Nos. | H | SPDC-2020-08-00000079 | SAP | 11742682
145 | WALK WAY TO NEW ESTUARY FLOWSTATION | 2020-07-18 | Severely warped Grating steps(thread) and Grating platform at approach to walk way. | Provide galvanized steel Grating, cut to size and install. 1.2m x 0.25m x 3Nos. 1.2m x 0.57m | H | SPDC-2020-08-00000079 | SAP | 11742682
146 | NEW ESTUARY FLOWSTATION | 2020-07-18 | BOAT LANDING Severely corroded Grating Platform. | Remove corroded Gratings. Provide galvanized steel Grating, cut to size and install. Area = 160 x 1.8m | H | SPDC-2020-08-00000079 | SAP | 11742682
147 |  | 2020-07-18 | Extremely corroded Handrails and Toe Boards | Remove and cart away extremely corroded Handrails. Provide galvanized Handrails of specified dimension, cut to size and weld as required. Prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 40mm dia. CHS, 1.5m x 19Nos. 1.2m x 17Nos. | H | SPDC-2020-08-00000079 | SAP | 11742682
148 |  | 2020-07-18 | Severe corrosion on Grating supports | Remove corrosion with hand tools, Prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 0.6m dia CHS, 280m length. | H | SPDC-2020-08-00000079
149 |  | 2020-07-18 | FENDER/FENDER SUPPORTS Severe corrosion with metal loss on Fender support. | Replace severely corroded and degraded Fender supports. Prepare surface and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 350mm dia. CHS, 8m x 25Nos. | H | SPDC-2020-08-00000079
150 |  | 2020-07-18 | Extreme corrosion with metal loss on bollard welded to Fender support. | Remove and cart away corroded bollard. Provide steel section of specified dimension, cut to size and weld. 200mm dia. CHS, 800mm long. | H | SPDC-2020-08-00000079
151 |  | 2020-07-18 | Missing Fender at boat landing. | Provide and install Rubberized Wharf Fenders, made up of Polythene materials with fiber glass reinforcement bars. 3m x 25Nos. | H | SPDC-2020-08-00000079
AFREMO A & B
152 | AFREMO A PLATFORM HELIDECK | 2019-05-19 | HELIDECK ACCESS PLATFORM Severely degraded Timber members on Access Platform | Provide and install hard wood to replace the degraded timber members. 2.3 x 0.32 x 0.07 x 5Nos. | H | SPDC-2019-07-00000086 | SAP
153 | AFREMO A PLATFORM BOAT LANDING | 2019-05-20 | Severely degraded Rubber Fenders. | Provide and install Rubber Wharf Fenders, made up of Polythene materials with fiber glass reinforcement bars. (7Nos.) | H | SPDC-2019-07-00000086 | SAP
154 | AFREMO A PLATFORM PILE FOUNDATION | 2019-05-20 | Severe corrosion and metal loss on Vertical Pipe Support (Column). | Remove corrosion by grit blasting, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 250mm dia. CHS, 2.2m x 5Nos. | H | SPDC-2019-07-00000086 | SAP
155 | AFREMO B TOILET DECK | 2020-07-18 | Severe corrosion with metal loss on Grating supports, Grating Platform and Handrails. | Remove corrosion by grit blasting, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. Grating supports: 200 x 100mm Channel, 2.8m long 80 x 80mm EAS, 8.2m long 300mm dia. CHS, 8.2m x 3Nos. 150mm dia. CHS, 15m long Grating: 1.5 x 1m. Handrails: 60mm dia. CHS, 1.8m x 27Nos. 1.3m x 19Nos. | H | SPDC-2020-08-00000079 | SAP
156 | AFREMO B BOAT LANDING | 2019-05-21 | Severely corroded Grating platform. | Provide galvanized steel Grating, cut to size and install. 8.3 x 1.4m. | H | SPDC-2019-07-00000086 | SAP
157 |  | 2019-05-21 | Severely degraded Fenders. | Provide and install Rubber Wharf Fenders, made up of Polythene materials with fiber glass reinforcement bars. (9Nos.) | H | SPDC-2019-07-00000086 | SAP
158 |  | 2019-05-21 | Coating failure, severe corrosion and metal loss on rungs for personnel access Ladder. | Remove corrosion by grit blasting, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. 12mm dia. mild steel, 0.35m x 4Nos. | H | SPDC-2019-07-00000086 | SAP
SOUTHBANK FLOWSTATION ACTIVITIES
159 | METERING SKID | 2018-06-14 | Steel Gantry - Overdue for Certification; due date – 01/04/2018. | Carry out recertification of Gantry. | H | SPDC-2018-07-00000135 | SAP
160 | FOT- SOUTHBANK 2ND CULVERT Guardrails | 2020-05-06 | Broken sections, failed and collapsed sections. | Replace broken section, weld and make good. -2m length of 100mm dia. CHS | H | SPDC-2020-05-00000044
161 | Approaches to Culvert | 2020-05-06 | Suspended road pavement due to erosion of its base materials; 1.8m into the road beneath the pavement. Pavement susceptible to sudden collapse. Wide Pothole at the edge of Culvert extending into the road pavement. A ditch (1m deep) observed by the Culvert wall within the pothole. | SEE RECOMMENDED ACTIONS FROM THE LAST INSPECTION REPORT - DOC. NO: SPDC-2018-1000000260 SEE RECOMMENDED ACTIONS FROM THE LAST INSPECTION REPORT – DOC. NO.: SPDC-2018-10-00000260 | H | SPDC-2020-05-00000044
162 | Culvert Barrel: Top Slab Soffit | 2020-05-06 | Spalled concrete with exposed corroded bottom Re-bars (16mm dia.) observed in each Culvert cell. (5.2 x 3m each cell |  | H
163 | River Channel Slope | 2020-05-06 | Failed concrete overlay and exposed Gabion Mattress structure (Geotextile and Chainlink) along River embankment |  | H
164 | Embankment/ Wingwall backfill | 2020-05-06 | Collapsed/eroded sections of the road embankment |  | H
165 | Guardrails | 2020-05-06 | Broken sections, Failed and collapsed sections. Mild to moderate corrosion on Handrails, Knee Rails and Posts |  | H
166 | Wingwalls and Headwalls | 2020-05-06 | Scouring of backfill materials underneath base of Wingwall | Remove the soil behind the wingwall carefully, compact in layers of 150mm to the finished level. Provide, mix and place concrete grade 30 to fill the area. Size = 150mm thick, 1m long and 0.6m wid | H
BENISEDE FLOWSTATION ACTIVITIES
| BANK 2: LP2 SEPARATOR, HP2 SEPARATOR & TEST 2 SEPARATOR | 2022-04-04 | Severe corrosion on drain pan | Remove corrosion with hand tools. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid coat and Polyurethane topcoat, or other approved coating materials to the prepared surface 12m x 6m | H | SPDC-2022-04-00000158
| BENISEDE JETTY TOPSIDE | 2022-04-05 | Steel pile casing Severe corrosion on steel pile casing | Remove corrosion with hand tool. Prepare surface and apply self priming Epoxy primer, Epoxy midcoat and Polyurethane topcoat, or other approved coating materials to the prepared surface 600mm dia. CHS; 2m x 2Nos | H | SPDC-2022-04-00000158
|  | 2022-04-06 | Unstable guardrail by jetty side | Prepare foundations of 200mm dia. For each post of the guardrail. 200mm x 10Nos. Provide, mix and place concrete grade 30 in foundation hole dug for the guardrail. 0.2m x 0.3m x 10Nos. | H | SPDC-2022-04-00000158
| DIESEL TANK SHED | 2020-04-04 | Missing and loosed aluminum roofing sheet | Provide and install aluminum roofing sheet on shed. 6m x 15m | H | SPDC-2022-04-00000158
| FLARE IGNITION POINT | 2022-04-04 | Severe scouring around Concrete Foundation N/B: 2021 scouring dimension: 80mm – 100mm Current scouring dimension: 150 – 200mm | Monitor scoured area periodically before any repair. Fill up area with sharp sand 1.5m x 0.5m x 0.95m depth | H | SPDC-2022-04-00000158
|  | 2022-04-04 | Suspended vertical ladder due to subsidence on concrete foundation | Monitor subsidence periodically before any repair. Reconstruct Concrete Floor using reinforced Concrete grade 30. 7.2m x 2.5m x 0.15m | H | SPDC-2022-04-00000158
| CORROSION INHIBITOR STORAGE TANK SHED | 2022-04-04 | Subsidence observed on Concrete. Severe scouring around Foundation and concrete ramp (Depth of scouring section 250mm – 350mm) | Monitor level of subsidence periodically before any repair. Provide, spread and compact sharp sand around Concrete Foundation and Concrete ramp.38m x 0.5m x 0.3m depth. Demolish and reconstruct Concrete ramp using grade 30 reinforced Concrete 5.5m x 4.2m x 0.15m depth | H | SPDC-2022-04-00000158
|  | 2022-04-04 | Broken section of bundwall | Remove and cart away broken section. Reconstruct broken section with concrete grade 25 and make good. 0.7m x 0.15m x 0.2m | H | SPDC-2022-04-00000158
| INLET MANIFOLD | 2021-08-06 | Grating Platform: Unstable section of Grating Platform. | Provide Grating clips for unstable section of Grating Platform.4Nos. |  | SPDC-2021-09-00000032
| DIESEL LOADING SHED | 2020-04-04 | Severe corrosion, perforations and coating failure on Roof steel support members | Provide, install and coat new Roof steel support members to replace severely corroded and perforated members. Prepare surface and apply self priming Epoxy primer, Epoxy midcoat and Polyurethane topcoat, or other approved coating materials to the prepared surface 60mm dia. CHS, 20m long | H | SPDC-2022-04-00000158
167 | HELICOPTER LANDING PAD (HELIPAD) MARKING | 2019-07-13 | Severely degraded coating and markings on concrete surface. | Remove degraded paint markings with hand tools, prepare surface and apply two coats of emulsion paint or other approved paint with markings on prepared surface. 18.1 x 18.1m | H | SPDC-2019-06-00000003 | SAP | 11735622
168 | WAITING SHELTER | 2019-07-13 | Moderate coating loss on Roof cladding.Moderate pitting corrosion on Roof steel members. | Prepare surface and apply selfpriming Epoxy primer, Epoxy mid-coat and Polyurethane topcoat, or other approved coating materials to the prepared surface. (4 + 2.5)m x 0.8m x 2Nos.Remove pitting corrosion with hand tools. Prepare surface and apply self-priming Epoxy primer, Epoxy mid-coat and Polyurethane topcoat, or other approved coating materials to the prepared surface. 100mm dia. CHS, 28m long 80mm dia. CHS, 36m long | H | SPDC-2019-06-00000003 | SAP | 11735622
| WELLHEAD 5 PLATFORM BOAT LANDING | 2021-08-07 | Missing Fenders | Provide fit-for-purpose reinforced Rubber Fenders. 0.2m x 0.2m x 2.5m x 4Nos. | H | SPDC-2021-10-00000004 | SAP
| WELLHEAD 3 PLATFORM UPPER DECK PLATFORM | 2021-08-07 | Unstable U-shaped Grating Platform | Provide and install U-shaped Grating Platform. |  | SPDC-2021-10-00000004
|  |  | Absence of grating clips on grating platform | Provide and install galvanized grating clips 12 Nos | H | SPDC-2021-10-00000004
| WELLHEAD 16 PLATFORM BOAT LANDING | 2021-08-07 | Missing and Moderate corrosion on Fender bolts | Provide and replace corroded bolts with galvanized bolts. 25mm dia.,16Nos | H | SPDC-2021-10-00000004
| WELLHEAD 16 PLATFORM LOWER DECK PLATFORM | 2021-08-07 | Warped/deflected Grating Platforms. | Provide and replace deflected Grating platforms 1.4m x 1m x 2Nos. | H | SPDC-2021-10-00000004
| WELLHEAD 16 PLATFORM UPPER DECK PLATFORM | 2021-08-07 | Loose Gratings due to missing Grating clips | Provide and install galvanized grating clips 8Nos. | H | SPDC-2021-10-00000004
| WELLHEAD 19 PLATFORM. BOAT LANDING | 2021-08-07 | Missing Fenders | Provide fit-for-purpose reinforced Rubber Fenders. 0.2m x 0.2m x 2.5m x 4Nos. | H | SPDC-2021-10-00000004
| WELLHEAD 6 PLATFORM UPPER DECK PLATFORM | 2021-08-07 | Observation Water ponding on Chequered plate Severe corrosion with metal loss and perforation on chequered plate platform | Cut and cart away chequered plate. Provide and install galvanized Grating platform 3.3m x 3.3m |  | SPDC-2021-10-00000004
| WELLHEAD 23 PLATFORM BOAT LANDING | 2021-08-07 | Bent and moderately corroded Fender bolts | Replace bent/moderately corroded Fender bolts 25mm dia., 2Nos. |  | SPDC-2021-10-00000004
| WELLHEAD 20 PLATFORM BOAT LANDING | 2021-08-07 | Degraded Fenders | Provide fit-for-purpose reinforced Rubber Fenders 0.2m x 0.2m x 2.5m x 4Nos. |  | SPDC-2021-10-00000004
| WELLHEAD 20 PLATFORM UPPER DECK PLATFORM | 2021-08-07 | Absence of Intrusion Detective System Cage (IDS) | Provide and install IDS Cage 3.3m x 2.5m x 2Nos |  | SPDC-2021-10-00000004
| WELLHEAD 11 PLATFORM LOWER DECK PLATFORM | 2021-08-07 | Missing Handrails. Warped and missing Grating Platform and Toe boards | Provide circular hollow section (CHS) and mild steel plates of specified dimensions, cut to size and welding. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid-coat and Polyurethane topcoat, or other approved coating materials to the prepared surface. Handrails: 35mm dia. CHS, 55.3m long Toe boards(Mild steel plate): 6.5m x 0.1m x 2Nos. Provide and install galvanized Grating on Grating support 3.3m x 1.2m x 2Nos |  | SPDC-2021-10-00000004
| WELLHEAD 18 PLATFORM BOAT LANDING | 2021-08-07 | Missing Fenders | Provide fit-for-purpose reinforced Rubber Fenders 0.2m x 0.2m x 2.5m x 4Nos |  | SPDC-2021-10-00000004
| WELLHEAD 18 PLATFORM LOWER DECK PLATFORM | 2021-08-07 | Missing Handrails | Provide circular hollow section (CHS) of specified dimensions for Handrail, cut to size and install. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid-coat and Polyurethane topcoat, or other approved coating materials to the prepared surface. Handrails: 35mm dia. CHS, 16.8m long |  | SPDC-2021-10-00000004
| WELLHEAD 18 PLATFORM UPPER DECK PLATFORM | 2021-08-07 | Absence of Intrusion Detective System Cage (IDS) | Provide and install IDS Cage 3.3m x 2.5m x 2Nos. |  | SPDC-2021-10-00000004
| WELLHEAD 1 PLATFORM BOAT LANDING | 2021-08-08 | Missing Fenders | Provide fit-for-purpose reinforced Rubber Fenders 0.2m x 0.2m x 2.5m x 4Nos. |  | SPDC-2021-10-00000004
| WELLHEAD 1 PLATFORM LOWER DECK PLATFORM | 2021-08-08 | Warp Handrails and Toe boards. Moderate coating failure on stanchions, diagonal bracings, bracing plates, Grating supports, Toe board and Handrails | Straighten warped section of Handrails and Toe boards using Hand tools. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid-coat and Polyurethane topcoat, or other approved coating materials to the prepared surface. Casing: 800mm dia. CHS, 2.5m long Bracing plates: 0.8m x 0.2m x 12Nos. Stanchions/diagonal bracings: 120mm dia. CHS, 8m long 60mm dia. CHS, 26.6m long 80mm dia. CHS, 14.4m long Handrails: 35mm dia. CHS, 55.3m long Grating Support: 100 x 60mm Channel, 25.2m long Toe boards: 6.5m x 0.1m x 2Nos. Vertical access Ladder: Flat bar– 2.7m x 0.05m x 2Nos. 1.9m x 0.05m x 4Nos. Rungs- 16mm dia. bar, 0.4m x 21Nos. |  | SPDC-2021-10-00000004
| WELLHEAD 21 PLATFORM BOAT LANDING | 2021-08-08 | Missing and degraded Wooden Fenders | Provide fit-for-purpose reinforced Rubber Fenders 0.2m x 0.2m x 2.5m x 4Nos |  | SPDC-2021-10-00000004
| WELLHEAD 14 PLATFORM BOAT LANDING | 2021-08-08 | Missing and degraded Wooden Fenders | Provide fit-for-purpose reinforced Rubber Fenders 0.2m x 0.2m x 2.5m x 4Nos |  | SPDC-2021-10-00000004
| WELLHEAD 4 PLATFORM BOAT LANDING | 2021-08-08 | Missing Fenders | Provide fit-for-purpose reinforced Rubber Fenders 0.2m x 0.2m x 2.5m x 4Nos |  | SPDC-2021-10-00000004
| WELLHEAD 9 PLATFORM BOAT LANDING | 2021-08-08 | Missing Fenders | Provide fit-for-purpose reinforced Rubber Fenders 0.2m x 0.2m x 2.5m x 4Nos |  | SPDC-2021-10-00000004
| WELLHEAD 9 PLATFORM LOWER DECK PLATFORM | 2021-08-08 | Warped section of Handrails and Access Ladder. Moderate coating failure on Steel well casing, stanchions, diagonal bracings, bracing plates, Grating supports, vertical access Ladder, Toe board and Handrails. | Straighten warped section of Handrails and Access Ladder. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid-coat and Polyurethane topcoat, or other approved coating materials to the prepared surface. Casing: 800mm dia. CHS, 2.5m long Bracing plates: 0.8m x 0.2m x 12Nos. Stanchions/diagonal bracings: 120mm dia. CHS, 8m long 60mm dia. CHS, 26.6m long 80mm dia. CHS, 14.4m long Handrails: 35mm dia. CHS, 55.3m long Grating Support: 100 x 60mm Channel, 25.2m long Toe boards: 6.5m x 0.1m x 2Nos. Vertical access Ladder: Flat bar– 2.7m x 0.05m x 2Nos. 1.9m x 0.05m x 4Nos. Rungs- 16mm dia. bar, 0.4m x 21Nos. |  | SPDC-2021-10-00000004
| WELLHEAD 2 PLATFORM BOAT LANDING | 2021-08-08 | Broken section of Fende | Provide fit-for-purpose reinforced Rubber Fenders and properly install/fix to Fender supports 0.2m x 0.2m x 2.5m x 1Nos. |  | SPDC-2021-10-00000004
174 | HELIPAD WALKWAY | 2019-07-12 | Severe cracks on walkway. | Open up cracks, provide, mix and treat cracks with rich sandcement mortar. 5.9m x 0.2m x 15mm | H | SPDC-2019-06-00000003 | SAP | 11735622
175 | PUMP HOUSE | 2019-07-12 | Severe corrosion/metal loss on drain pan beside Centrifugal Pump. | Provide and install new drain pan. Prepare surface and apply selfpriming Epoxy primer, Epoxy midcoat and Polyurethane topcoat, or other approved coating materials to the prepared surface. 6.5m x 1.5m x 2Nos. | H | SPDC-2019-06-00000003 | SAP | 11735622
176 | WATER TREATMENT PLANT | 2019-07-12 | Torn and Severely corroded Chain-link Door. | Provide and replace torn and severely corroded Chain-link. 2m x 0.9m | H | SPDC-2019-06-00000003 | SAP | 11735622
177 | WATER TREATMENT PLANT | 2019-07-12 | Severe corrosion/coating failure on Tank and Skid. | Remove corrosion with hand tools. Prepare surface and apply self-priming Epoxy primer, Epoxy mid-coat and Polyurethane topcoat, or other approved coating materials to the prepared surface. Tank: 2.9m x 0.8m x 2Nos. 2.9m x 1.1m x 2Nos. 1.6m x 1.5m x 2Nos. Skid: 250 x 140mm IPE, 1.5m x 3Nos. 200 x 75mm Channel, 0.9m x 6Nos. | H | SPDC-2019-06-00000003 | SAP | 11735622
179 | FLOWSTATION STATION ATTENDANT BUILDING | 2021-08-06 | Bathroom & Toilet: Missing and Severely degraded Doors. | Replace degraded Doors with fine finish plastic toilet doors Size = 2.1 x 0.9m x 2Nos. | H | SPDC-2021-09-00000032 | SAP | 11735622
180 |  |  | Sewage Pit: Full at the time of assessment | Evacuate and cart away content of tank | H |  | SAP
181 | PUMP HOUSE | 2020-03-25 | Severe corrosion/metal loss on drain Pan beside | Provide and install new drain Pan. Prepare surface and apply self-priming Epoxy primer, Epoxy mid coat and Polyurethane topcoat, or other approved coating materials to the prepared surface. 6.5m x 1.5m x 2Nos. | H | SPDC-2020-04-00000163 | SAP
OGUNU ACTIVITY
182 | MAIN JETTY (HEAVY MARINE VESSELS) | 2019-09-20 | FIRE HYDRANT OPPOSITE ARMY POST Collapsed section of pavement Centrifugal Pump. | Demolish collapsed section of concrete pavement and excavate to 100mm depth beneath the pavement. Provide, spread and compact 2 layers of 150mm deep sharp sand. Provide, cut and fix mild steel BRC 65 mesh reinforcement in concrete. Provide, mix and place C30 concrete. Vol. = 4 x 1.5 x 0.2m | H | SPDC-2019-10-00000008 | SAP
183 |  | 2019-09-20 | Missing Jetty Fenders. | Provide and install rubber Fenders. 68Nos | H | SPDC-2019-10-00000008 | SAP
184 |  | 2019-09-20 | Broken and warped anchor for vertical access Ladder. | Provide, cut to length and weld new anchors to replace the broken section. 16mm dia. Rebar 1.2m length. | H | SPDC-2019-10-00000008 | SAP
185 | RAMP JETTY | 2019-09-20 | Missing Fenders. | Provide and install rubber Fenders. 38Nos. | H | SPDC-2019-10-00000008 | SAP
186 | LIGHT MARINE VESSEL(LMV) | 2019-09-20 | Collapsed concrete edge section behind the Jetty Sheet Pile. 3.2 x 2 x 1.8m | Provide, fill the collapsed section with laterite sand. 3.2 x 2 x 1.5m. Provide, cut and fix mild steel BRC 65 mesh reinforcement in concrete. Are = 3.2 x 2m. Provide, mix and place concrete grade 30 on prepared area. Vol. = 3.2 x 2 x 0.15m. | H | SPDC-2019-10-00000008 | SAP
187 |  | 2019-09-20 | Severely degraded concrete staircase and missing Handrails. 1.2 x 0.4 x 8Nos. Handrails: 35mm dia. CHS, 6m x 2Nos. | Prepare surface by chiseling off concrete from steps using power tool. Provide and install wooden formworks. 2.4 x 1 x 2Nos. Provide, mix, place and compact Grade 30 concrete Volume of concrete = 1.2 x 0.4 x 0.15m x 2Nos. Fabricate and install steel Handrails on Jetty staircase. Prepare surface with hand tools and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. Handrails: 35mm dia. CHS, 6m x 2Nos. | H | SPDC-2019-10-00000008 | SAP
188 | FUEL DUMP AREA | 2019-09-20 | Failed/collapsed concrete step leading to fuel dump section. | Demolish the collapsed section of the concrete steps and cart away spoils from site. Provide, fill and compact area with laterite to a depth of 400mm. 1.2 x 1.5 x 0.6m. Provide, cut to size, bend to shape and fix high yield steel reinforcement of 10mm dia. at a spacing of 300mm. 9Nos. Provide, mix, place and compact Grade 30 concrete. 1.2 x 1.5 x 0.15m. (Thread 200mm, riser 100mm). | H | SPDC-2019-10-00000008 | SAP
189 |  | 2019-09-20 | Severe scouring underneath Citadel Fence concrete foundation and Beam | Provide, spread and compact scoured section with sharp sand sloping towards Sheet Pile wall to a depth of 400m. Size = 45 x 3 x 0.4m. Provide, cut and fix mild steel BRC 65 mesh reinforcement in concrete. Area = 45 x 3. Provide, mix and place C30 concrete sloped towards Sheet Pile wall. Vol. = 45 x 3 x 0.15m | H | SPDC-2019-10-00000008 | SAP
190 | HELIPAD SIDE WALL | 2019-09-20 | Subsidence and cracks at base of Helipad wall. | Scarify sections to 100mm below finished grade and cart away debris. Compact scarified area. Provide, mix, place and compact Grade 30 concrete Size = 26.9 x 1.2 x 0.15m | H | SPDC-2019-10-00000008 | SAP
OTUMARA ACTIVITY
| STATION ATTENDANT HUT | 2021-10-23 | Bathroom Severely corroded Door | Provide and install new Door to replace severely corroded one Size = 2.1m x 0.8m | H | SPDC-2021-11-00000071
|  | 2021-10-23 | Broken shower | Replace broken shower with new one | H | SPDC-2021-11-00000071
| CHEMICAL SHED | 2021-10-23 | Severely corroded chainlink and torn section of Chain-lin | Remove and cart away existing chain-link. Replace existing chainlink with new ones. Area = 35.5m x 1.7m | H | SPDC-2021-11-00000071
191 | OTUMARA FLOWSTATION: DIESEL STORAGE TANK SHED | 2021-10-23 | Roof Missing section of Aluminium Roofing Sheet | Provide and install new Aluminium Roofing Sheet to replace torn one Area = 5m x 1m | H | SPDC-2021-11-00000071
|  | 2021-10-23 | Severe corrosion with perforations and coating failure on Roof Steel Member | Cut off severely corroded Roof Steel Member. Provide, cut to size and weld in place new Roof Steel Member. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface 100mm dia. CHS, 8m long | H | SPDC-2021-11-00000071
192 | ELEVATED WATER TANK | 2021-10-23 | Severe corrosion with metal loss and coating failure on PFC Horizontal bracings at base of Steel supports | Remove and cart away corroded horizontal bracings. Provide, cut to size and weld Parallel Flange Channel (PFC) at the base of steel supports. 100mm x 50mm PFC, 2.5m x 4Nos. | H | SPDC-2021-11-00000071
193 | INLET MANIFOLD | 2021-10-23 | Missing Grating clips on Grating platform | Provide and install galvanized Grating clips 24Nos. | H | SPDC-2021-11-00000071
|  | 2021-10-23 | Severely Corroded thread supports of personal access staircase | Remove corrosion with hand tools. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface 0.3m x 0.1m x 18Nos. | H | SPDC-2021-11-00000071
| BANK3 BACK PRESSURE MANIFOLD | 2021-10-23 | Absence of Grating clips on Grating Platforms | Provide and install galvanized Grating clips 24Nos. | H | SPDC-2021-11-00000071
|  | 2021-10-23 | Failed Grating by skid of back pressure manifold due to insufficient grating supports | Provide and install sufficient grating support on failed sections 100mm x 50mm Channel, 1.2m long Reinstall Grating including grating clips Area= 1.5m x 1.2m 8Nos of Grating clips | H | SPDC-2021-11-00000071
| TEST SEPARATORS 2 | 2021-10-23 | Severe corrosion with metal loss and Water ponding on Drain Pan | Carefully remove Gratings over affected area and provide additional Drain ports. Remove corrosion by light grit blasting. Prepare surface and apply self-priming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface Drain Pan: 7.5m x 1m x 2Nos. 5m x 1.5m x 2Nos. Drain Ports: 6Nos | H | SPDC-2021-11-00000071
| LP SEPARATOR 4 (V-303) | 2021-10-23 | Absence of Grating clips | Provide and install galvanized Grating clips 16Nos | H | SPDC-2021-11-00000071
|  |  | Moderate – severe corrosion on Drain Pans | Carefully remove Gratings over affected area and remove corrosion from drain pans by grit blasting. Prepare surface and apply self-priming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface. Area = 3.5m x 7.2m | H | SPDC-2021-11-00000071
|  |  | Collapsed/unstable Gratings due to insufficient gating supports | Provide and install sufficient grating support on collapsed sections 100mm x 50mm Channel, 4.2m long Reinstall Grating and include galvanized Grating clips. 4Nos. | H | SPDC-2021-11-00000071
|  |  | Severe corrosion with metal loss on section of Drain pan | Carefully remove Grating over affected area. Cut off and cart away from site corroded Drain pan. Provide mild steel plate, cut to size, weld as required to skid. Area = 5.5m x 1.5m. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface 5.5m x 1.5m | H | SPDC-2021-11-00000071
194 | SURGE VESSEL 3 (V-304) | 2021-10-23 | Water ponding, Moderate – severe corrosion on Drain Pan | Carefully remove Gratings over affected area. Create additional drain ports. Remove corrosion by light grit blasting. Prepare surface and apply self-priming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface Drain Ports: 6Nos. Drain Pan: 6.5m x 5.4m | H | SPDC-2021-11-00000071
195 |  |  | Missing Bolts on vertical Access Ladder | Replace and re-install missing Bolts on vertical Access Ladder 12mm dia., 2Nos | H | SPDC-2021-11-00000071
196 | BANKS2 LP SEPARATOR 2 & 3(202) | 2021-10-23 | Misaligned Grating due to absence of Grating clips | Provide and install galvanized Grating clips 10Nos. | H | SPDC-2021-11-00000071
197 | FREE LIQUID KNOCKOUT VESSEL | 2021-10-23 | Severe corrosion, metal loss and torn section of Drain pan | Carefully remove Grating over affected area. Cut off and cart away from site corroded Drain pan. Provide mild steel plate of specified thickness, cut to size, and weld to skid. Area = 3.7m x 1.8m x 5mm thickness. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface Area = 12.2m x 8.5m | H | SPDC-2021-11-00000071
198 | SURGE VESSEL 2(V-204) | 2021-10-23 | Absence of Grating clips on Grating Platform | Provide and install galvanized Grating clips 24Nos. | H | SPDC-2021-11-00000071
199 | PRESSURE MANIFOLD BETWEEN BANK 2 & BANK 1 | 2021-10-23 | Absence of Grating clips on Platform | Provide and install galvanized grating clips 18Nos. | H | SPDC-2021-11-00000071
200 |  | 2021-10-23 | Broken section of Handrail | Weld Handrail to post. | H | SPDC-2021-11-00000071
201 | TEST SEPARATOR (V101), HP SEPARATOR (V102), LP SEPARATOR (V103), | 2021-10-23 | Severe corrosion, Metal loss and torn section of Drain pan on skid of test separator | Cut off, cart away and replace affected area of drain pan. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface 3.5m x 1m x 2Nos. | H | SPDC-2021-11-00000071
202 |  | 2021-10-23 | Severe corrosion with metal loss on Grating support of test separator skid | Cut off and cart away corroded Grating support. Provide IPE beam of specified dimensions, cut to size and weld as required. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface 150mm x 150mm IPE, 6.5m long | H | SPDC-2021-11-00000071
203 | SURGE VESSEL 1 (V-104) | 2021-10-23 | Severe corrosion, metal loss and torn section of drain pan | Cut off, cart away and replace affected area of drain pan. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface Area = 4.5m x 1.5m | H | SPDC-2021-11-00000071
204 |  | 2021-10-23 | Severe corrosion with metal loss on flange and web of beam of Grating support | Cut off, cart away and replace affected grating support.300mm x 180mm IPE, 2.5m long. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface 300mm x 180mm IPE, 2.5m long. 250mm x 130mm IPE, 18m long. 100mm x 50mm PFC, 3m long | h | SPDC-2021-11-00000071
205 |  | 2021-10-23 | Severe corrosion and metal loss on clamp of fire hydrant pump | Remove corrosion by grit blasting. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface 400mm x 250mm x 2Nos. | H | SPDC-2021-11-00000071
206 | PUMP HOUSE | 2021-10-23 | ROOF GUTTER Broken section of downspout | Provide, install and welding 100mm dia. Steel downspout pipe 2.5m long | H | SPDC-2021-11-00000071
|  | 2021-10-23 | Severe corrosion with metal loss on Drain Pan | Cut off, cart away and replace affected area of drain pan. Area = 1.6m x 1m | H | SPDC-2021-11-00000071
|  | 2021-10-23 | Severe corrosion, metal loss and coating failure on Grating Supports | Remove corrosion with hand tools. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface Grating Supports: 250mm x 100mm IPE, 56.4m long | H | SPDC-2021-11-00000071
|  | 2021-10-23 | Severe corrosion, metal loss and coating failure on Parallel Flange Channel (PFC) support underneath Storm Water Tan | Provide, cut to size, install and weld in place new PFC to replace severely corroded one. Prepare surface and apply self-priming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface 100mm x 50mm PFC, 2.5m long | H | SPDC-2021-11-00000071
|  | 2021-10-23 | Moderate – severe corrosion on Drain pan | Remove corrosion by grit blasting. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface Area = 10.5m x 2.5m | H | SPDC-2021-11-00000071
|  | 2021-10-23 | Absence of Grating clips on Grating Platforms | Provide and install galvanized Grating clips On Pump shield Grating Platform 64Nos | H | SPDC-2021-11-00000071
|  | 2021-10-23 | Pump 4 Severe corrosion with metal loss on Grating support beside handrails in front of Pump 4 | Provide, cut to size, install and weld in place new Grating support to replace severely corroded one. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface 80mm x 80mm EAS, 1m long | H | SPDC-2021-11-00000071
|  | 2021-10-23 | Severely corroded and broken welded section of Grating support in front of Pump 4 | Weld support to Primary beam. Remove corrosion with hand tools. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface 80mm x 80mm EA, 0.9m long | H | SPDC-2021-11-00000071
|  | 2021-10-23 | Severe corrosion with metal loss at web of steel beam Grating support in front of Pump 4 | Remove corrosion with hand tools. Provide and weld stiffener steel plates to web of beam. Prepare surface and apply self-priming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface 180mm x 3.5m length | H | SPDC-2021-11-00000071
|  | 2021-10-23 | Pump 8 Severe corrosion with metal loss at the base of pipe steel supports in front of Pump 8 | Provide, cut to size, weld in place steel plates to strengthen and reinforce base of severely corroded pipe steel supports. Prepare surface and apply self-priming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface Pipe Steel Supports: 200mm x 80mm PFC, 1m x 2Nos. 10mm Thick Steel Plates: 0.3m x 0.2m x 2Nos, 0.3m x 0.08m x 2Nos. | H | SPDC-2021-11-00000071
|  | 2021-10-23 | Severe corrosion with metal loss on flanges of grating support beside Pump 8 | Provide, cut to size, install by welding in place new IPE grating support to replace severely corroded one. 240mm x 180mm IPE, 3.5m long (3m long steel plate). Remove corrosion with hand tools. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface 240mm x 180mm IPE, 3.5m long (3m long steel plate) 160mm x 65mm Channel, 0.3m long (0.3m long steel plate) | H | SPDC-2021-11-00000071
|  | 2021-10-23 | Handrail facing the River Warped section of cantilevered Grating supports and Handrai | Straighten warped section. Prepare surface and apply self-priming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface 250mm x 150mm IPE, 1.5m x 5Nos. 200mm x 50mm PFC, 1.8m x 5Nos | H | SPDC-2021-11-00000071
|  | 2021-10-23 | Severe corrosion on cantilevered Grating supports | Prepare surface and apply selfpriming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface 290mm x 130mm IPE, 46m long. 250mm x 150mm PFC, 37.5m long. 200mm x 50mm PFC, 37.5m long | H | SPDC-2021-11-00000071
|  | 2021-10-23 | Between Pumps 4 & 6 Severe corrosion with metal loss on Grating Supports | Remove corrosion with hand tools. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface Grating Supports: 250mm x 130mm IPE, 5m long | H | SPDC-2021-11-00000071
|  | 2021-10-23 | Behind entire length of pump house Severe corrosion with metal loss and coating failure on Grating supports | Remove corrosion with hand tools. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface Grating Supports: 250mm x 130mm IPE, 156m long | H | SPDC-2021-11-00000071
|  | 2021-10-23 | Toe boards Warped toe boards along sections of grating supports | Straighten out warped toe boards | H | SPDC-2021-11-00000071
| BESIDE CLOSED DRAIN | 2021-10-23 | Severe corrosion and metal loss on grating supports | Remove corrosion with hand tools. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid coat and Polyurethane top coat, or other approved coating materials to the prepared surface Grating Supports: 280mm x 160mm IPE, 45.4m long | H | SPDC-2021-11-00000071
| MANIFOLD WITH CITADEL CAGE | 2021-10-23 | Missing Handrails for Staircase landing | Provide and install missing Handrails for Staircase landing 45mm dia. CHS, 1.3m long | H | SPDC-2021-11-00000071
| CENTRAL CONTROL ROOM | 2021-10-23 | SUSPENDED CEILING Missing and moderate to severely degraded Ceiling boards (with water patches around vents) due to consistent soaking of condensed water from the HVAC vent | Remove and cart away the degraded Ceiling boards. Provide and install new Ceiling boards 0.6m x 0.6m x 35Nos. | H | SPDC-2021-11-00000071
|  | 2021-10-23 | HVAC Vents directly supported against the Ceiling boards | Dismantle the HVAC vent supports pushing against the Ceiling boards. Drill through the vent support clamp to widen the hold down bolt hole. Provide and install suspension rods through the bolt hole to anchor the HVAC vent clamps to the Roof cladding off the Ceiling boards. | H | SPDC-2021-11-00000071
| 11KVA SWITCHGEAR ROOM | 2021-10-23 | Defective emergency Door lever handle | Provide and install new emergency Door lever handle (1No.) | H | SPDC-2021-11-00000071
|  | 2021-10-23 | Defective Door lock/handle | Provide and install new Door lock/handle (1No.) | H | SPDC-2021-11-00000071
| 0.4KVA SWITCHGEAR ROOM | 2021-10-23 | Defective Door locks/handles (both entrance doors) | Provide and install new Door locks/handles to replace defective ones 2Nos. | H | SPDC-2021-11-00000071
|  | 2021-10-23 | Defective Elastomeric Door rubber seal | Provide and install new Elastomeric Door rubber seal to replace defective one 1No. | H | SPDC-2021-11-00000071
|  | 2021-10-23 | EMERGENCY EXIT DOOR Defective Door lock/handle | Provide and install new Door lock/handle to replace defective one 1No | H | SPDC-2021-11-00000071
| VERTICAL FLARE STRUCTURE STAIRCASE | 2021-10-23 | Broken/detached Gratings | Provide, install and weld Equal Angle Steel sections as Grating supports on both sides of thread together with bolted connections 80mm x 80mm EAS, 0.3m x 48Nos. 10mm dia.,96Nos. | H | SPDC-2021-11-00000071
| JETTY CONCRETE STAIRCASE | 2021-10-23 | Broken and detached Handrails | Re-install Handrail using Concrete C30 to hold firm the post at both ends 0.3m x 0.15m x 0.15m | H | SPDC-2021-11-00000071
| SUPPORT PILE COLUMNS | 2021-10-23 | Perforations observed on the steel casing for the support piles | Carry out detailed pile inspection and apply steel jacket extending over whole damaged area. 410mm dia. CHS, 1.2m x 4Nos. | H | SPDC-2021-11-00000071
| SHEET PILE WALLS | 2021-10-23 | Moderate – severe corrosion and coating failure on sheet pile walls along perimeter of jetty | Remove corrosion with hand tools. Prepare surface and apply self-priming Epoxy primer, Epoxy mid-coat and Polyurethane top coat, or other approved coating materials to the prepared surface 400m x 3m | H | SPDC-2021-11-00000071
| FENDERS | 2021-10-23 | Missing and severely degraded wooden Fenders | Provide and install fit-forpurpose rubber Fenders to replace severely degraded wooden Fenders0.3m x 0.3m x 2m x 54Nos. | H | SPDC-2021-11-00000071
ESCRAVOS ACTIVITIES
213 | POLLUTION CONTROL CARAVAN | 2021-10-25 | Severely degraded ceiling boards | Remove and cart away degraded Ceiling boards. Provide and install new Ceiling boards 9.9m x 0.6m x 2Nos | H | SPDC-2021-12-00000010
214 | CHEMICAL SHED | 2021-10-25 | Severely corroded and broken perimeter chain-link on dwarf wall | Replace corroded perimeter chainlink with new one Area = 22.2m x 2.3m | H | SPDC-2021-12-00000010
215 | DIESEL STORAGE TANK | 2021-10-25 | Severe degradation and cracks on concrete Bundwalls, staircase and pavement | Open up cracked sections. Provide, mix and treat cracks/degradation with sand cement mortar Bundwall:10.2m x 0.225m x 3mm 17.2m x 0.225m x 25mm Pavement/Concrete Floor: 0.4m x 0.3m x 25mm x 3Nos. Concrete staircase: 0.2m x 0.15m x 0.1m | H | SPDC-2021-12-00000010
216 | FLARE STRUCTURE | 2021-10-25 | Warped and broken Handrails as a result of falling Trees | Cut down all trees that are 6m close to walkway. Straighten and weld warped/broken sections of Handrail to Flare walkway | H | SPDC-2021-12-00000010
219 | PERIMETER FENCE ALONG FRONT OF FLOW STATION | 2019-10-29 | Severely degraded and torn sections of the Chain-link Fence; inadequate Fence posts. | Remove inadequate Posts. Cut out and cart away severely warped/torn sections of the Fence. Provide, and install new Fence posts and Chain link Fence. Fence: 175m x 3m Posts: 140mm dia. CHS, 3m x 14Nos | H | SPDC-2019-11-00000030
220 | PERIMETER FENCE BESIDE FLARE WALKWAY GATE | 2019-10-29 | Severely corroded section of Chain link Fence with metal loss | Cut out and cart away severely corroded section of the Chain-link Fence. Provide and install new Chain-link Fence 75m x 2.8m | H | SPDC-2019-11-00000030
221 | PERIMETER FENCE BESIDE WATER TREATMENT PLANT & GEN. HOUSE | 2019-10-29 | Severely corroded/torn Chain-link Fence | Cut out and cart away severely corroded section of the Chain-link Fence. Provide and install new Chain-link Fence 120m x 2.8m | H | SPDC-2019-11-00000030
222 |  | 2019-10-29 | Severely warped top rails supporting the Chain-link Fence. | Provide and replace the warped top rail support. 50mm x 50mm EAS, 2.5m long | H | SPDC-2019-11-00000030
223 |  | 2019-10-29 | Severe erosion/ scouring underneath Chain-link Fence | Provide, lay and compact sand stabilised with 6% Ordinary Portland cement and fill up eroded area underneath Fence. 20m x 2m x 0.4m | H | SPDC-2019-11-00000030
224 |  | 2019-10-29 | Severely corroded and degraded razor/barb wire on Chain link Fence along entire perimeter of Fence | Cut and remove the severely degraded razor wire and cart away. Provide and install new razor wire for Chain link perimeter Fence 600m long | H | SPDC-2019-11-00000030
| NORTHBANK ACTIVITIES | 2021-02-11
| NORTHBANK-YOKRI ELECTRIC POWER TIMBER POLES SURFACE CONDITION | 2021-11-30 | Termite infestation observed at the base of 2 nos. Timber Poles installed by the Telecom Mast area. | Provide and install 2 Nos. Concrete Poles to replace the severely degraded Timber Poles | H | SPDC-2021-12-00000075
225 | NORTH BANK FLOWSTATION: INLET MANIFOLD | 2021-02-11 | Scaffold materials used as Handrails. Absence of Handrails on Grating Platform | Provide and install Handrails. Prepare surface and apply selfpriming Epoxy primer, Epoxy mid-coat and Polyurethane topcoat or other approved coating materials to the prepared surfaces = 42.4mm dia. CHS, 65m long | H | SPDC-2021-03-00000050
226 | STATION ATTENDANT BUILDING | 2021-02-11 | Defective Door Key | Provide and install complete set of Door Key - 1No. | H | SPDC-2021-03-00000050
227 |  |  | Severely degraded ceiling boards | Replace degraded ceiling boards with new ones 0.6m x 0.6m x 6 | H | SPDC-2021-03-00000050
228 | NORTHBANK JETTY: FENDERS | 2021-02-11 | Severely degraded Timber Fenders at Boat Landing | Remove and cart away degraded Fenders and Fender Accessories completely. Provide fit for purpose fixed Rubberised Fenders system (e.g., Arch, D-Type or Cylindrical Fender Systems). Size = 230 x 180mm; 1m Long, 20Nos. | H | SPDC-2021-03-00000050
229 | HANDRAILS ON JETTY |  | Absence of Handrails on Jetty hard stand | Provide materials for Guardrails, fabricate, weld and install properly. Prepare surface of Handrails and apply self-priming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. Handrails: 110mm dia., 54m long Knee Rails: 110mm dia., 54m long Posts: 110 dia., 25m long | H | SPDC-2021-03-00000050
230 | SHEET PILES | 2021-02-11 | Severely corroded sheet Piles | Remove corrosion by grit blasting, prepare surface and apply selfpriming Epoxy primer, Polyurethane topcoat or other approved coating materials on the prepared surfaces. Area = 90m x 1.8m All works to be done at LLWL. | H | SPDC-2021-03-00000050
231 | JETTY CONCRETE SURFACE | 2021-02-11 | Failed concrete section on LHS of approach to Military Shed at the Jetty | Prepare area of failed section. Provide, mix and place grade C30 reinforce concrete on prepared surface. Broom finish and make good. Size = 8.5m x 3.3m x 0.2m | H | SPDC-2021-03-00000050
232 | RAMP | 2021-02-11 | Severely silted Jetty Ramp Concrete surface not visible | Clear debris off the Jetty Ramp Area = 7m x 4m | H | SPDC-2021-03-00000050
YOKRI ACTIVITY
233 | YOKRI FLOWSTATION: TELECOM TOWER | 2021-02-12 | Severely degraded ceiling boards | Carry out Roof leakage repairs. Provide and install new Ceiling boards to replace degraded ones Size = 0.6m x 0.6m x 17Nos. | H | SPDC-2021-03-00000050
234 | YOKRI COMPRESSION STATION: COMPRESSION SHED | 2021-02-12 | Severely corroded Roof Gutte | Remove and cart away degraded Roof Gutter. Provide and install new Roof Gutter Size = 70m x 0.8m | H | SPDC-2021-03-00000050
235 |  | 2021-02-12 | Extremely corroded Switch Gear Box | Replace corroded Switch Gear Box with new one - 1No | H | SPDC-2021-03-00000050
236 | YOKRI HELIPAD:PERIMETER CHAIN LINK FENCE | 2021-02-12 | Severely worn out, missing at some sections. | Replace degraded/missing sections of the chain link fence. 75m length by 3m high. | H | SPDC-2021-03-00000050
237 | WELLHEADS 85/76 | 2021-02-12 | Severely corroded Cellar Grating cover and Grating supports | Remove and cart away from site corroded Gratings and Grating supports. Provide and install galvanized Gratings Area = 5.5m x 3m Provide and install equal angle iron Grating supports = 80 x 80mm EAS; 17.6m long | H | SPDC-2021-03-00000050